## SSO SUMMARY
The first two sections count the number of events and volume amounts for each type of Sanitary Sewer Overflow (SSO) for each municipality and in total | [29 empty] | This secion keeps track of the approximate gallons spilled from SSOs by municipality - a combined total of CSOs and SSOs is on the Reached Water Summary Tab
Municipality | # of SSO Events | # of NPDES Permitted Bypasses | # ot TOTAL EVENTS | All Events Total Estimated Gallons | # Reached Water | # Excessive Flows - Storm Event | Volume (gallons) Excessive Flows - Storm Event | # Excessive Flows - Snow Melt | Volume (gallons) Excessive Flows - Snow Melt | # Electrical Equipment Failure | Volume (gallons) Eletrical Equipt Failure | # Mechanical Equipment Failure | Volume (gallons) Mech Equipt Failure | # Other - Sewer Break | Volume (gallons) Other - Sewer Break | # Other - Contractor Damaged Sewer | Volume (gallons) Other - Sewer Break | # Other - Water Main Break | Volume (gallons) Other - Water Main Break | # Sewer Line Blockage - Grease | Volume (gallons) Line Blockage - Grease | # Sewer Line Blockage - Rags | Volume (gallons) Line Blockage - Rags | # Sewer Line Blockage - Roots | Volume (gallons) Line Blockage - Roots | # Sewer Line Blockage - Other | Volume (gallons) Link Bolckage - Other | # Unknown Cause | Volume (gallons) Unknown Cause | Unnamed Waterbody (gallons) | Avery Brook (gallons) | Bantam River (gallons) | Bridgeport Harbor / LIS (gallons) | Bruce Pond (gallons) | Byram River (gallons) | Cedar Creek / LIS (gallons) | Connecticut River (gallons) | East Mountain Brook / Hallock Brook (gallons) | East Swamp Brook (gallons) | Farmington River (gallons) | Five Mile Pond (gallons) | Fort Hill Brook (gallons) | Goodwives River (gallons) | Great Swamp (gallons) | Highland Lake (gallons) | Hockanum River (gallons) | Housatonic River (gallons) | Island Brook (gallons) | Lake Forest (gallons) | Little River (gallons) | Long Island Sound (gallons) | Mad River (gallons) | Moosup River (gallons) | Naugatuck River (gallons) | New Haven Harbor (gallons) | Old Field Creek (gallons) | Oyster River (gallons) | Park River (incl N, S & Conduit) (gallons) | Pequonnock River (gallons) | Piper Brook (gallons) | Quinnipiac River (gallons) | Rooster River (gallons) | Salmon Brook (gallons) | Shetucket River (gallons) | Steele Brook (gallons) | Stillmans Pond (gallons) | Success Lake (gallons) | Thames River (gallons) | Trout Brook (gallons) | West River (gallons) | Willimantic (gallons)
Beacon Falls | 2 | 0 | 2 | 53300 | 1 | 1 | 50000 | [20 empty] | 1 | 3300 | [24 empty] | 50000
Branford | 3 | 0 | 3 | 2500 | 0 | [16 empty] | 3 | 2500 |  |  | 0 | [12 empty] | 50
Bloomfield (MDC) | 1 | 0 | 1 | 95 | 0 | [22 empty] | 1 | 95
Bridgeport (East & West) | 24 | 21 | 45 | 67704030 | 26 | 22 | 67693100 | [12 empty] | 13 | 2950 | 2 | 550 |  |  | 8 | 7430 | [5 empty] | 6508100 | 450 |  | 61185000 | [22 empty] | 6825 | [6 empty] | 350 | 1500
Bristol | 5 | 0 | 5 | 1955 | 0 | [14 empty] | 1 | 85 | 1 | 85 | 2 | 935 | 1 | 850
Cheshire | 2 | 0 | 2 | 1400 | 0 | [14 empty] | 2 | 1400 | [8 empty] | 700
Cromwell (Mattabassett) | 1 | 0 | 1 | 2433645 | 1 | 1 | 2433645 | [29 empty] | 2433645
Danbury | 5 | 0 | 5 | 1950 | 0 | [14 empty] | 2 | 350 |  |  | 2 | 1500 | 1 | 100
Darien | 5 | 0 | 5 | 10150 | 3 |  |  |  |  | 1 | 5525 |  |  |  |  | 1 | 4500 |  |  | 1 | 15 | 1 | 100 | 1 | 10 | [17 empty] | 15 | [7 empty] | 10025
East Hartford (MDC) | 2 | 0 | 2 | 1070 | 1 | [6 empty] | 1 | 975 | [12 empty] | 1 | 95 | [9 empty] | 975
East Haven (GNHWPCA) | 1 | 0 | 1 | 50 | 0 | [14 empty] | 1 | 50
East Lyme | 2 |  | 2 | 570 | 1 | [6 empty] | 1 | 300 |  |  | 1 | 270
East Windsor | 2 | 0 | 2 | 475 | 0 | [16 empty] | 1 | 450 |  |  |  |  | 1 | 25
Fairfield | 7 | 0 | 7 | 6750 | 1 | [14 empty] | 3 | 2200 | 3 | 550 |  |  | 1 | 4000 | [34 empty] | 4000
Glastonbury | 2 | 0 | 2 | 2850 | 1 | [14 empty] | 1 | 2700 | 1 | 150 | [39 empty] | 2700
Greenwich | 1 | 0 | 1 | 23000 | 1 | [8 empty] | 1 | 23000 | [19 empty] | 23000
Groton (City, Town & USN) | 17 | 0 | 17 | 1126508 | 5 | [6 empty] | 2 | 1102600 | 4 | 8606 |  |  |  |  | 6 | 15179 | 2 | 18 |  |  | 2 | 100 | 1 | 5 | 8500 | [11 empty] | 1100000 | [25 empty] | 16
Hamden (GNHWPCA) | 4 | 0 | 4 | 581 | 0 | [14 empty] | 3 | 536 |  |  | 1 | 45
Hartford (MDC) | 10 | 0 | 10 | 54685 | 5 |  |  | 1 | 20000 |  |  | 1 | 10 | 1 | 25200 | 1 | 7000 | 1 | 2000 | 2 | 190 | [6 empty] | 3 | 285 | 95 | [6 empty] | 95 | [20 empty] | 29000
Killingly | 4 |  | 4 | 700 | 1 | [6 empty] | 1 | 0 | [8 empty] | 3 | 700 | [17 empty] | 250
Litchfield | 4 | 0 | 4 | 156455 | 2 |  |  |  |  | 2 | 5 | 2 | 156450 | [18 empty] | 156450
Manchester | 2 | 0 | 2 | 300 | 0 |  |  |  |  | 1 | 100 | [16 empty] | 1 | 200
Mansfield (UCONN) | 2 | 0 | 2 | 9100 | 0 | [8 empty] | 2 | 9100
Meriden | 1 | 0 | 1 | 95 | 1 | [18 empty] | 1 | 95 | [35 empty] | 95
Middletown | 1 | 0 | 1 | 2000 | 0 | [10 empty] | 1 | 2000
Milford | 5 | 0 | 5 | 4700 | 0 | [18 empty] | 1 | 100 | 3 | 4550 | 1 | 50
Montville | 3 | 0 | 3 | 1500 | 0 | [6 empty] | 2 | 1000 | 1 | 500
Naugatuck | 2 | 0 | 2 | 190 | 0 | [8 empty] | 1 | 95 | [6 empty] | 1 | 95
New Hartford | 1 | 0 | 1 | 360 | 1 | [16 empty] | 1 | 360 | [14 empty] | 360
New Haven (GNHWPCA) | 12 | 49 | 61 | 132690928 | 50 | 50 | 132689400 |  |  |  |  | 1 | 40 | [6 empty] | 4 | 164 | 1 | 95 | 2 | 213 |  |  | 3 | 1016 | [25 empty] | 132689100 | [5 empty] | 40
New London | 1 | 0 | 1 | 45 | 0 | [18 empty] | 1 | 45
New Milford | 2 | 0 | 2 | 193 | 1 | [14 empty] | 1 | 90 |  |  | 1 | 103 | [21 empty] | 90
Newington (MDC) | 4 | 0 | 4 | 1349190 | 2 | 2 | 1349000 |  |  |  |  | 1 | 95 | [14 empty] | 1 | 95 | [30 empty] | 1349000
Norfolk | 1 | 0 | 1 | 100000 | 0 | [22 empty] | 1 | 100000
Norwalk | 14 | 0 | 14 | 2895 | 2 | [14 empty] | 1 | 25 | 2 | 1550 | 1 | 9 | 2 | 90 | 8 | 1221 | 45 | [20 empty] | 100
Norwich | 8 | 0 | 8 | 25818 | 4 |  |  |  |  | 1 | 18630 | 3 | 3788 | [8 empty] | 3 | 1600 |  |  |  |  | 1 | 1800 | [34 empty] | 1800 |  |  |  | 22417
Orange | 1 | 0 | 1 | 300 | 0 | [8 empty] | 1 | 300
Plainfield | 2 | 0 | 2 | 151800 | 1 | [6 empty] | 1 | 150000 |  |  |  |  | 1 | 1800 | [33 empty] | 1800
Plymouth | 2 | 0 | 2 | 640 | 1 | [8 empty] | 1 | 190 | [10 empty] | 1 | 450 |  |  | 450
Putnam | 1 | 0 | 1 | 100 | 0 | [8 empty] | 1 | 100
Ridgefield | 5 | 0 | 5 | 585 | 2 |  |  |  |  | 2 | 180 | 1 | 25 | [6 empty] | 2 | 380 | [22 empty] | 180
Seymour | 4 | 0 | 4 | 16330 | 1 | [8 empty] | 1 | 15800 | [6 empty] | 1 | 30 | 2 | 500 | [24 empty] | 15800
Shelton | 2 | 0 | 2 | 45 | 0 | [6 empty] | 1 | 25 | 1 | 20
Simsbury | 4 | 0 | 4 | 500 | 1 | [18 empty] | 3 | 400 |  |  | 1 | 100 | [10 empty] | 100
South Windsor | 7 | 0 | 7 | 338544 | 7 |  |  |  |  | 4 | 322944 | [10 empty] | 2 | 10700 |  |  |  |  | 1 | 4900 |  | 10700 | [5 empty] | 327844
Southington | 3 | 0 | 3 | 540 | 0 | [14 empty] | 2 | 90 |  |  | 1 | 450
Stafford | 1 | 0 | 1 | 13500 | 1 |  |  |  |  | 1 | 13500 | [59 empty] | 13500
Stamford | 9 | 0 | 9 | 541 | 2 |  |  |  |  | 1 | 5 | [8 empty] | 2 | 160 |  |  |  |  | 4 | 311 | 2 | 65 | [21 empty] | 260
Stratford | 4 | 0 | 4 | 1867000 | 4 | 1 | 1125000 |  |  | 1 | 250000 | [16 empty] | 2 | 492000 | [17 empty] | 1867000
Suffield | 1 | 0 | 1 | 420 | 0 | [10 empty] | 1 | 420
Trumbull | 7 | 0 | 7 | 820095 | 5 | [8 empty] | 6 | 812095 | 1 | 8000 | [12 empty] | 8000 | [17 empty] | 10000 | 5000 | [9 empty] | 788000
Vernon | 5 | 0 | 5 | 142606 | 4 | [6 empty] | 1 | 127106 | 1 | 10000 | [12 empty] | 3 | 5500 | [16 empty] | 142556
Waterbury | 10 | 0 | 10 | 803230 | 3 | 1 | 800000 | [12 empty] | 1 | 2000 | 2 | 625 | 2 | 230 | 4 | 375 | [24 empty] | 400 |  | 800000 | [10 empty] | 150
West Haven | 19 | 0 | 19 | 20008615 | 11 | 3 | 20002000 |  |  | 3 | 210 | 5 | 6165 | [6 empty] | 2 | 18 | 2 | 30 | 1 | 20 | 2 | 170 | 1 | 2 | [25 empty] | 20006122 | 100 | 1150 | [12 empty] | 1000
West Hartford (MDC) | 18 | 0 | 18 | 16919194 | 8 | 10 | 16916995 | [6 empty] | 1 | 0 | 1 | 950 |  |  | 2 | 14 | 1 | 950 | 2 | 190 |  |  | 1 | 95 | [30 empty] | 4270000 | [8 empty] | 3243950
Westport | 3 | 0 | 3 | 2500 | 0 | [8 empty] | 2 | 1500 | [10 empty] | 1 | 1000
Windham | 1 | 0 | 1 | 45 | 0 | [16 empty] | 1 | 45
Winsted | 1 | 0 | 1 | 500 | 1 | [10 empty] | 1 | 500 | [27 empty] | 500
SUMMARY | 273 | 70 | 343 | 246857663 | 162 | 91 | 243059140 | 1 | 20000 | 17 | 611099 | 24 | 1548579 | 25 | 906506 | 8 | 23640 | 2 | 3800 | 52 | 28596 | 34 | 21183 | 24 | 4845 | 31 | 19521 | 34 | 610754 | 17790 | 10700 | 156450 | 6508100 | 450 | 23000 | 61185000 | 2762559 | 360 | 50 | 100 | 250 | 1100000 | 15 | 180 | 500 | 142556 | 1867090 | 10000 | 5000 | 15800 | 10385 | 400 | 1800 | 850000 | 152695222 | 100 | 1150 | 29000 | 794825 | 5619000 | 135 | 4000 | 2700 | 1800 | 150 | 350 | 1500 | 22433 | 3243950 | 1000 | 13500
[6 empty] | 343 | 246857663
[30 empty] | TOTAL REACHED WATER: |  | 237099350
Data Caveats
While DEEP is the storehouse for the SRTK data, DEEP makes the following caveats:
· All data is submitted by publicly owned wastewater treatment plants and publicly owned satellite collection systems.
· DEEP does not issue notifications about individual discharges, they are inputted by the reporters for each municipality and issued by the electronic system automatically.
· The reports are being submitted by the municipalities in a short time frame after discovery of a discharge and specific details may not be known.
· Data is estimated based on the existing systems, models, and personal knowledge of the sewer systems by the reporters.
· Data quality, especially volumes, is not checked by DEEP.
· The electronic program allows for zero duration, short durations and zero quantities for volumes.
· Addresses may not be entered by municipalities in a way that allows the parts of the address to be separated nor with an exact location.
· Multiple notifications may be sent for the same discharge since municipalities need to submit daily and termination reports for ongoing discharges.
· Duplicate reports and reports submitted that resulted in zero flow may be rescinded in the system.

## BEACON FALLS
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
BEACON FALLS | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-09-05 | 02:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | High wet well alarm | 50,000 | Effluent flow chart | Yes | Naugatuck River | 2022-09-05 | 03:00 AM | 50,000 gallons | 50000 |  | increased RAS back to aeration and stopped all side flows to the wet well | Beacon Falls | 411 Lopus Rd, Beacon Falls, CT
BEACON FALLS | Closed | Sewage Bypass | Dry | 2022-11-29 | 12:15 PM | Pump Station | Raw Sewage | Unknown | ongoing investigation | resident called | 20Gal./min | by eye | No | none | 2022-11-29 | 03:00 PM | 3300 gallons | 3300 |  | It appeared to fix itself, someone may have dumped into it thinking it was part of the collection sy | Beacon Falls | 3 Pines Bridge Rd, Beacon Falls, CT
53300

## BRANFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRANFORD | Closed | Sewage Bypass | Dry | 2022-12-08 | 07:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  |  |  |  | No |  | 2022-12-08 | 08:45 AM | 500 gallons. | 500 |  | jetted sewerline | Branford | 40 Laurel Hill Rd, Branford, CT
BRANFORD | Closed | Sewage Bypass | Dry | 2022-07-21 | 06:00 AM | Lateral - Public | Raw Sewage | Sewage Line Blockage - Rags |  | Resident called | 1000 gallons | visual | No |  | 2022-07-21 | 07:15 AM | 1000 gals | 1000 |  | jetted sewer line | Branford | 17 Nicole Rd, Branford, CT
BRANFORD | Closed | Sewage Bypass | Dry | 2022-03-03 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags |  | worker noticed | 1000 gallons | visual | No |  | 2022-03-03 | 01:15 PM | 1000 gallon | 1000 |  | jetted sewer line | Branford | 15 Donna Ln, Branford, CT
2500

## BRIDGEPORT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-02-04 | 06:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Excessive rain and snow melt caused higher than normal flows to plant | Street level indicator, miltronics | NA | Flow meter | Yes | Bridgeport Harbor | 2022-02-04 | 08:45 AM | 1.04mg. | 1040000 |  | Rain slowed down | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-06-27 | 04:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain in a short period of time | Operations monitoring street level indicator | 1.31 mg. | Flow meter | Yes | Bridgeport Harbor - long island sound | 2022-06-27 | 07:30 PM | 1.31 mg. | 1310000 |  | Rain stopped | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-07-18 | 07:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | High flows due to heavy rain | street level indicator | 1.33mg. Bypass lasted 2.75 hours and total rain was 1.63" | flow meter | Yes | Bridgeport Harbor - Long Island Sound | 2022-07-18 | 10:00 AM | 1.33MG | 1330000 |  | Rain stopped | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-07-18 | 01:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | An accumulation of grease and rags along with high flows due to heavy rain. | Home owner notified the WPCA | Not permitted to enter private residence to determine volume. | NA | No |  | 2022-07-18 | 02:00 PM | Not permitted to enter private residence to determine volume. | 100 |  | Field operations found line surcharged and and immediately jetted and cleared the line. An accumul | Bridgeport | 105 Gem Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-08-02 | 12:15 PM | Manhole | Raw Sewage | Other | Excessive amount of toilet paper | Zoo employees notified WPCA and field operations crew was dispatched. | minimal amount | visual | No |  | 2022-08-02 | 01:15 PM | under 5 gallons | 5 |  | Jetted the line and cleared backup | Bridgeport | 1875 Noble Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-09-02 | 11:45 AM' | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Blockage | Incident was reported to Bridgeport WPCA | 30-40 gpm for 3 hours and 15 minutes. | visual | Yes | Pequannock River | 2022-09-15 | 03:30 PM | 6,825 gallons | 6825 |  | On 9-2-22 when incident was reported at 11;45 am Field Operations responded cleared the blockage a | Bridgeport | 725 Housatonic Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-09-04 | 02:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Main line back up | Incident was discovered by the home owner who called the Bridgeport WPCA to report the incident. | Unknown. Staff not permitted to enter private residence. | Homeowner complained of sewage smell and backup in basement.. Quantity undetermined | No |  | 2022-09-04 | 05:00 PM | Homeowner reported a sewage smell in her basement.. Also unknown amount of sewage in the basement. | 100 |  | The main line was jetted and cleaned. | Bridgeport | 98 Foster Square, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-09-06 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Sewer line blockage due to debris and heavy rain caused a backup in the basement at 95 Gem Ave. | Homeowner notified the Bridgeport WPCA | NA | NA | No |  | 2022-09-06 | 02:30 PM | NA Staff not allowed to enter private residence to estimate volume | 100 |  | Staff jetted main line and cleared clog | Bridgeport | 95 Gem Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-09-06 | 11:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Bypass due to heavy rain | Street level indicator / flow meter | 2.08mg | Flow meter | Yes | Bridgeport Harbor /long Island Sound | 2022-09-06 | 04:00 PM | 2.08 mg. | 208000 |  | Rain tapered off and plant went out of bypass. | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-09-13 | 08:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | On 9-13-22 at 8;45am the Bridgeport WPCA received notification of an overflowing manhole located at | WPCA was notified of manhole overflowing. | NA Overflow had stopped by the time staff arrived. | NA | No |  | 2022-09-13 | 09:30 AM | N/A When staff arrived on site there was no overflow. Staff proceeded to clean up debris and jetted | 100 |  | When staff arrived on site there was no overflow. Staff proceeded to clean up debris and jetted se | Bridgeport | 155 Carrie St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-09-13 | 01:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Main line surcharged possibly due to heavy rain earlier today and debris in the line. | Home owner notified Bridgeport WPCA | Staff not permitted to enter private residence. Quantity unknown | Staff not permitted to enter private residence. | No |  | 2022-09-13 | 02:30 PM | N/A Staff not permitted to enter private residence to estimate volume. | 100 |  | Main line was surcharged. possibly due to heavy rain earlier in the day . Quantity unknown. Staff do | Bridgeport | 80 Taft Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-09-13 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | There was heavy rain last night and early this morning. The high flows and debris in the line caused | Home owner discovered backup and notified Bridgeport WPCA | Staff not permitted to enter private residence. | Staff not permitted to enter private residence. Quantity unknown | No |  | 2022-09-13 | 12:15 PM | Quantity unknown. Staff not permitted to enter private residence | 100 |  | Field Operations personnel Jetted main line clearing blockage. | Bridgeport | 75 Rusling Pl, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-09-13 | 07:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Street level indicator / flow meter | NA | Flow meter | Yes | Bridgeport Harbor/ Long Island Sound | 2022-09-13 | 10:00 AM | 1.41 mg | 1410000 |  | Rain ended and flow decreased and plant was able to come out of bypass. | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-09-26 | 12:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Combination of grease and rags. | Bridgeport resident notified the WPCA | less then 500 gallons | Visual determination | Yes | Bruce Pond | 2022-09-26 | 01:45 PM | less then 500 gallons | 450 |  | Main line was jetted and a large amount of rags and grease was removed. | Bridgeport | 1905 Barnum Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-10-05 | 09:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | Combination of grease, rags and wipes. | Home owner notified Bridgeport WPCA | N/A Staff not permitted to enter private property. | N/A Staff not permitted to enter private property. | No |  | 2022-10-05 | 09:15 AM | N/A Staff do not enter private property | 100 |  | Staff Cleared clog in main line. | Bridgeport | 98 Foster Square, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-10-14 | 01:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Influent flow meter , street level indicator | 1.21 mg | flow meter | Yes | Bridgeport harbor/ long Island Sound | 2022-10-14 | 03:30 AM | 1.21mg | 1210000 |  | Rain subsided | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-10-19 | 11:15 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | The sewer line was blocked with grease and caused the catch basin to overflow. Field operations imm | WPCA received a call for an overflowing catch basin. | 1500 gallons | visual determination. | Yes | Success Lake | 2022-10-19 | 12:00 PM | 1500 gallons | 1500 |  | Field operations cleared grease from the main line | Bridgeport | Broadbridge Rd, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-11-09 | 02:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Home owner notified the Bridgeport WPCA | N/A Not permitted to enter private property. | N/A Not permitted to enter private property. | No |  | 2022-11-09 | 02:45 PM | Unknown | 100 |  | Field Operations cleared blockage in main line | Bridgeport | 123 Sunshine Cir, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-11-10 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease buildup in main line | Home owner notified the Bridgeport WPCA | N/A Staff not permitted to enter private residences | N/A Staff not permitted to enter private residences | No |  | 2022-11-10 | 12:00 PM | N/A Staff not permitted to enter private residence | 100 |  | Field Operations personnel jetted main line and cleared blockage | Bridgeport | 2135 Boston Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-11-14 | 05:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags | The blockage was caused by grease, rags and wipes. | Home owner notified the Bridgeport WPCA | N/A Staff not permitted to enter private residence | N/A Staff not permitted to enter private residence | No |  | 2022-11-14 | 07:00 AM | N/A Staff not permitted to enter private residence | 100 |  | The blockage in the main line was jetted and cleared by 7am. | Bridgeport | 1297 Pembroke St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-12-10 | 12:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Combination of grease and rags | Home owner contacted the Bridgeport WPCA | Personnel are not permitted to enter private property therefore the amount bypassed cannot be determ | Personnel are not permitted to enter private property therefore the amount bypassed cannot be determ | No |  | 2022-12-10 | 01:15 PM | Undetermined. Staff not permitted to enter private residence | 100 |  | Main line was jetted and debris was removed | Bridgeport | 358 Hawley Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-12-15 | 10:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease caused back up | Home owner notified the Bridgeport WPCA | N/A Personnel not permitted to enter private residence. | N/A Personnel not permitted to enter private residence. | No |  | 2022-12-15 | 11:30 AM | N/A Personnel not permitted to enter private residence to estimate volume | 100 |  | Main line was jetted and grease blockage was cleared. | Bridgeport | 259 Dover St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2022-12-15 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage | Home owner notified the Bridgeport WPCA | N/A Staff not permitted to enter private property to determine volume. | N/A Staff not permitted to enter private property to determine volume. | No |  | 2022-12-15 | 02:45 PM | N/A Staff not permitted to enter private property to determine volume. | 100 |  | Field operations staff jetted main line and the line was flowing by 2;50pm. | Bridgeport | 596 Pearl Harbor St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-12-16 | 08:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags caused the back up | Home owner notified the Bridgeport WPCA | N/A Staff not permitted to enter private property to determine bypass volume in the house . However | N/A Staff not permitted to enter private property to determine bypass volume in the house. However t | Yes | Stillmans Pond | 2022-12-16 | 11:15 AM | 350 gallons | 350 |  | Field operations staff Jetted main line and cleared grease and rag blockage. | Bridgeport | 1315 Boston Ave, Bridgeport, CT
6518430
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-01-17 | 03:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | unknown | unknown | Yes | cedar creek long island sound | 2022-01-17 | 10:45 AM | 9.38 MGD | 9380000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2022-02-04 | 07:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | Unknown | Flow Totalizer | Yes | Cedar Creek Long Island Sound | 2022-02-04 | 10:45 AM | 2.88 MGD | 2880000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-02-22 | 08:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Miltronics Street Level indicator , Flow meter | 2.415mg | Flow meter | Yes | Cedar Creek , Long Island Sound | 2022-02-22 | 10:15 PM | 2.415 mg | 2415000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-03-25 | 01:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | Unknown | Unknown | Yes | Cedar Creek Long Island Sound | 2022-03-25 | 06:00 AM | 3.75 MG | 3750000 |  | Excess flow ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-04-08 | 11:45 PM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | observation | unknown | Flow Totalizer | Yes | cedar creek long island sound | 2022-04-08 | 08:30 AM | 10.10 MGD | 10100000 |  | Storm Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-04-19 | 01:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | 9.5 MGD | Flow Totalizer | Yes | Cedar Creek Long Island Sound | 2022-04-19 | 08:45 AM | 9.5 MGD | 9500000 |  | Storm Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-06-09 | 07:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual observation | 2.33 MGD | Flow Totalizer | Yes | Cedar Creek Long Island Sound | 06/09/2022 | 10:00 AM | 2.33 MG | 2330000 |  | Storm Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-06-27 | 04:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual | 1.51 MGD | Flow Totalizer | Yes | cedar creek long island sound | 2022-06-27 | 08:00 PM | 1.51 MGD | 1510000 |  | Storm Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-07-18 | 06:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual observation | 2.9 mgd | flow totalizer | Yes | cedar creek long island sound | 2022-07-18 | 11:00 PM | 2.9 mgd | 2900000 |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2022-08-10 | 08:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by homeowner | unknown | N/A | No |  | 2022-08-10 | 10:30 | 100 gallons estimated | 100 |  | Field Operations responded immediately and jetted the main line to remove grease and rags. | Bridgeport | 336 Benham Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-09-06 | 10:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Street level indicator. flow meter | 4.09mg | Flow meter | Yes | Cedar Creek / long Island Sound | 2022-09-06 | 05:00 PM | 4.09mg. | 4090000 |  | rain tapered off and plant resumed normal operations | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-09-13 | 06:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | Unknown | Unknown | Yes | Cedar Creek Long Island Sound | 2022-09-13 | 11:30 AM | 3.44 MGD | 3440000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-10-13 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual opservation | 1.83MG | Flow Totalizer | Yes | Cedar creek long island sound | 2022-10-14 | 02:30 AM | 1.3MG | 1300000 |  | Storm ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-10-24 | 12:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual observation | 4.36MG | Flow Totalizer | Yes | cedar creek long island sound | 2022-10-24 | 03:45 PM | 4.36MG | 4360000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2022-10-30 | 12:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by homeowner | unknown | unknown | No |  | 10/30/2022 | 02:00 PM | 100 gallons | 100 |  | Field Operations responded immediately and jetted the main line to remove grease and rags. | Bridgeport | 303 Coleman St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-11-11 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | 1.69 MG | Flow Totalizer | Yes | Cedar Creek Long Island Sound | 2022-11-11 | 10:30 PM | 1.69 MG | 1690000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2022-11-30 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Resident Called In | 100 Gal | Visual Observation | No |  | 11/30/2022 | 11:00 AM | 100 gallons estimated | 100 |  | Field Operations responded immediately and jetted the main line to remove the grease and rags. | Bridgeport | Woodlawn Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-12-06 | 11:45 PM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | Unknown | Flow Totalizer | Yes | Cedar Creek Long Island Sound | 2022-12-07 | 01:00 PM | 1.54 | 1540000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2022-12-11 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by Local Police | Unknown | Unknown | No |  | 2022-12-11 | 01:00 PM | 100 gallons estimated | 100 |  | Field Operations responded immediately and jetted the main line to remove grease and rags. | Bridgeport | 96 Manhattan Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2022-12-20 | 07:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | At 7:25 am this evening the homeowner at 120 Lorraine St. notified the Bridgeport WPCA of a sewage b | unknown | N/A | No |  | 2022-12-20 | 21:30 | 100 gallons estimated | 100 |  | Field Operations responded immediately and jetted the main line to remove the grease and rags. | Bridgeport | 120 Lorraine St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2022-12-27 | 09:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Called inn by Jimmy Rooter | unknown | unknown | Yes | Long Island Sound | 2022-12-27 | 23:45 | 100 gallons estimated | 100 |  | Field Operations responded immediately and jetted the main line to remove grease and rags. | Bridgeport | Noble Ave, Bridgeport, CT
61185600
67704030

## BRISTOL
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2022-02-05 | 05:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Sewer Division video inspected line on 2/7/22. Found roots in the line. Believed to be the cause of | Received a possible stoppage call from Simomne Corriveau at 96 Mercier Avenue | 50 to 100 gallons | Based on amount described by homeowner at 96 Mercier Avenue. | No |  | 2022-02-05 | 06:00 PM | 50 to 100 gallons | 85 |  | Line was jet cleaned to remove blockage. | Bristol | 181 Mercier Ave, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2022-06-23 | 02:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Buildup of grease in the line was cause of the blockage. Bypassed into the basement of house 69 Doro | Received possible stoppage call from Heidi Caruso from the Water division. Cathy, homeowner of 69 Do | 50 to 100 gallons | Based on description from homeowner. | No |  | 2022-06-23 | 02:45 PM | 50 to 100 Gallons | 85 |  | yes | Bristol | 69 Dorothy Rd, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2022-02-01 | 10:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Bristol staff found approximately a 6" square piece of plastic sewer pipe is what caused the stoppag | Bristol Water division received a call for a possible water main break. They contacted Sewer divisio | 500 to 1000 gallons | based on amount discharging out of the manhole and elapsed time of the SSO | No |  | 2022-02-01 | 11:45 PM' | 500 to 1000 | 850 |  | Staff jetted the line which dislodged the piece of plastic pipe. It was removed via the downstream m | Bristol | 216 Witches Rock Rd, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2022-04-11 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | Combination of roots, grease and rags. | Received call from Bristol Water Department | 500 to 1000 gallons | Based on elapsed time of the stoppage and amount discharging out of the manhole when staff arrived o | No |  | 2022-04-11 | 11:30 AM | 500 to 1000 gallons | 850 |  | Line was jet cleaned. Rags, grease and root ball were removed via a manhole | Bristol | 74 Farmington Ave, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2022-05-06 | 08:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | blockage is a combination of grease and roots. | Received a possible stoppage call from homeowner at 18 Benham Street | 50 to 100 gallons | Based on the quantity homeowner relayed to staff. | No |  | 2022-05-06 | 08:45 AM | 50 to 100 gallons | 85 |  | Line jet cleaned. | Bristol | 4 Benham St, Bristol, CT
1955

## BROOKFIELD
This report not counted
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
BROOKFIELD | Closed | Sewage Bypass | Dry | 2022-01-04 | 11:00 AM | Lateral - Private | Raw Sewage | Unknown | This bypass is not in the Brookfield WPCA Sewer Service area and was referred to Local Health | CALL | 0 | Not in the BWPCA service area - not a reportable incident | No |  | 2022-01-04 | 11:15 AM | 0 |  | This incident was referred to local health as it did not occur in the Brookfield WPCA sewer service | Brookfield | 24 High Ridge Rd, Brookfield, CT

## CHESHIRE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
CHESHIRE | Closed | Sewage Bypass | Dry | 2022-08-20 | 03:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | excess grease backing up the sewer line breaching the manhole | phone call to police and they called me | <1000 gallons | report time until resolution and line level was receding when crew arrived | No |  | 08/20/2022 | 04:15 AM | <1000 gallons | 950 |  | report time until resolution and line level was receding when crew arrived | Cheshire | 1700 Highland Ave, Cheshire, CT
CHESHIRE | Closed | Sewage Bypass | Dry | 2022-02-12 | 06:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | operator found it while in the area | under 300 gallons | visual inspection and estimation | No |  | 2022-02-12 | 10:00 AM | <500 gallons | 450 |  | jetted the lines down stream to free the grease and keep the line moving | Cheshire | 1721 Highland Ave, Cheshire, CT
1400

## DANBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2022-03-13 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | Called in by resident | 200gal | Visual Estimate | No |  | 2022-03-13 | 12:00 PM | 200gal | 200 |  | jetted and cut with root cutter | Danbury | 7 Topstone Dr, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2022-03-13 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | Called in by resident in area | 150-200gal total | Visual estimate | No |  | 2022-11-13 | 12:30 PM | 150+/- | 150 |  | Vac/Jet/Chem Treat | Danbury | 7 Topstone Dr, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2022-10-18 | 01:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by property owner | .5gpm | Visual Estimate | No |  | 2022-10-18 | 04:00 PM | 1000gal | 1000 |  | Line jetted and vacuumed | Danbury | 7 Shalvoys Ln, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2022-01-03 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by resident | 500gal | Visual Estimate | No |  | 2022-01-03 | 12:00 PM | 500gal | 500 |  | jetted | Danbury | 32 Grove Pl, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2022-01-15 | 08:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Concrete Failure in manhole | Called in by resident | 100 total gal | visual estimate | No | NA | 2022-01-15 | 09:00 AM | 100gal | 100 |  | Removed | Danbury | 4 Knapps Ln, Danbury, CT
1950

## DARIEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
DARIEN | Closed | Sewage Bypass | Dry | 2022-07-06 | 08:30 AM | Lateral - Private | Raw Sewage | Other | Excavation Machine forced valve stem on LPSS lateral shut off valve to breaking point. | Reported. emergency CBYD | 5 GPM | visual observation | Yes | Long Island Sound | 2022-07-06 | 10:30AM | Estimated quantity 4,500 gallons total released sewage. | 4500 |  | contractor repaired sewer lateral. | Darien | 12 Harbor Rd, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2022-11-22 | 06:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | weeping smh | 15 gal | estimated by visual inspection, 5 gal/3 min | Yes | catch basins to Goodwives River | 2022-11-22 | 07:00 AM | 15 gallons | 15 |  | line cleared | Darien | West Ave, Darien, CT
DARIEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-19 | 05:15 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | generator running, poor voltage output. Gen output at times. | High wet well, high channel, generator running. | 3 SMH's in vicinity of PS overflowed into CB's on the street which eventually discharge to LIS. 5,5 | Visual observation. 50, 10, and 5 GPM each SMH for 85 minutes | Yes | Long Island Sound | 2022-04-19 | 07:00 AM | 5,525 gallons | 5525 |  | Power restored | Darien | 170 Nearwater Ln, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2022-05-16 | 00:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | Resident called, could not flush toilet. Plumber stated was not the residents problem. | Approx 10 gallons | Visual, upon clearing the blockage the released flow slowly rose and breached the top of the manhole | No |  | 2022-05-16 | 00:00 AM | 10 gal | 10 |  | line cleared. | Darien | 322 Middlesex Rd, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2022-01-31 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | resident with slow toilet | 100 gallons | visual estimate of weeping SMH in grass area. | No | N/A | 2022-01-31 | 10:15 AM | 100 gallons | 100 |  | Jet rodder deployed to clear blockage | Darien | 64 Noroton Ave, Darien, CT
10150

## EAST LYME
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
EAST LYME | Closed | Sewage Bypass | Dry | 2022-09-14 | 01:00 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure |  | Vac contractor notified East Lyme Sewer Dept. | 300 gallons | visual estimate | No |  | 2022-09-14 | 03:15 PM | 300 Gallons | 300 |  | Vac contractor notified East Lyme Sewer Dept. | East Lyme | 141 Main St, East Lyme, CT
EAST LYME | Closed | Sewage Bypass | Dry | 2022-06-08 | 03:30 PM | Sewer Main | Raw Sewage | Other | Contractor damaged sewer main while installing sewer lateral. | On-site inspector reported damaged sewer main | 270 Gallons | Visual estimation | Yes | Black Point Back Bay /Pattaganset River | 2022-06-08 | 05:00 PM | 270 Gallons | 270 |  | Main repaired and put back into service. | East Lyme | 94 Old Black Point Rd, East Lyme, CT
570

## EAST WINDSOR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
EAST WINDSOR WPCF | Closed | Sewage Bypass | Dry | 2022-11-28 | 04:30 PM | Sewer Main | Raw Sewage | Unknown | Main line backed up, caused unfinished basement to back up with raw sewage at 203 Main Street, East | Home owner contacted Police Department, who then contacted WPCF Facility. | tbd | waiting for operators to clear plug and report back | No |  | 2022-11-28 | 07:00 PM | Minimal amount of wastewater backed up, all contained within property basement. | 25 |  | Line cleared with Vac-Con by Municipal Operations Team, cleanup instigated with private firm (ServeP | East Windsor | 203 Main St, East Windsor, CT
EAST WINDSOR WPCF | Closed | Sewage Bypass | Dry | 2022-03-18 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Line Blockage - Grease/Rags clogging pipe at Chimney. | Staff observed issue while doing Pump Station and Trouble area checks. | 50 - 500 gallons total. | Estimated by staff onsite. | No |  | 2022-03-18 | 10:30AM | 50 - 500 gallons total. | 450 |  | Debris cleaned by staff with Grapple Pole, all returned to normal. | East Windsor | 5 Phelps Rd, East Windsor, CT
475

## FAIRFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2022-11-03 | 11:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Uncapped pipes in basement , also a floor drain that has an unknown discharge point | Building owner contacted Fire department , who then contacted WPCF | 100 gallons | Visual estimate | No |  | 2022-11-03 | 12:15 PM | 100 Gallons | 100 |  | line was jetted to break plug in line | Fairfield | 167 Old Post Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-14 | 08:45 PM | Manhole | Raw Sewage | Other | Grease | sewer inspector | 1500 Gallons total | Visual Estimate | No |  | 2022-04-14 | 10:30 PM | 1500 gallons | 1500 |  | jetted line to break plug | Fairfield | Sunnyridge Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2022-10-29 | 11:15 AM | Lateral - Public | Raw Sewage | Sewage Line Blockage - Rags | manhole frame is offset allowing debris to enter line | called in by resident | 200 gallons | visual estimate | No |  | 2022-10-29 | 12:45 PM | 200 GALLONS | 200 |  | JETTED LINE TO BREAK BLOCKAGE. Informed DOT. DOT fixed manhole. Fairfield CCTV's the lateral and | Fairfield | 309 Round Hill Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2022-10-29 | 11:15 AM | Lateral - Public | Raw Sewage | Sewage Line Blockage - Rags | frame of manhole is offset allowing surface debris to enter the lateral. | called into plant by a resident | 200 gallons | visual estimate | No |  | 2022-10-29 | 12:15 PM | 200 Gallons | 200 |  | flushed from town manhole upstream to service connection manhole breaking service plug . | Fairfield | 309 Round Hill Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2022-05-26 | 04:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | We believe it was sticks and yard debris. Upon flushing line, there was heavy grease build up in the | Homeowner | 25000 gallons -unsure when it stopped. | Estimate | Yes | Rooster River | 2022-05-27 | 06:00 AM | 4000 gallons, no definitive time as to when it stopped, as it was reported to an e-mail of a person | 4000 |  | By-pass stopped on it's own, as material passed through and dislodged debris. | Fairfield | 195 Flushing Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2022-12-18 | 05:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | received a call from FFld police dept | 600 gallons | visual estimate | No |  | 2022-12-18 | 06:45 PM | 600 gallons | 600 |  | jetted the line to break a grease plug | Fairfield | 10 Green Acres Ln, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2022-08-29 | 02:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | called in by DPW | 150 gal | visual estimate | No |  | 2022-08-29 | 03:15 PM | 150 gallons | 150 |  | Blockage cleared and line was given a good cleaning. Will monitor more frequently. | Fairfield | 140 Melville Dr, Fairfield, CT
6750

## GLASTONBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
GLASTONBURY | Closed | Sewage Bypass | Dry | 2022-03-27 | 07:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Discovered by MDC, who notified Glastonbury PD, then notified WPC on call. | 2700 gallons | calculated by estimated flow rate. | Yes | Salmon brook | 2022-03-28 | 08:00 AM | 2700 gallons | 2700 |  | flushing of line by Highway | Glastonbury | 38 Wyllys St, Glastonbury, CT
GLASTONBURY | Closed | Sewage Bypass | Dry | 2022-10-25 | 12:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Discovered by Housing Authority staff. | approximately 150 gallons | about 5 GPM for 30 mins. | No |  | 2022-10-25 | 12:45 PM | 150 gallons | 150 |  | Town maintenance staff cleared the sewer pipe blockage with high pressure jet nozzle. | Glastonbury | 13&15 Deming Rd, Glastonbury, CT
2850

## GNHWPCA
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-05-17 | 10:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Sewer back up was caused by Grace in the sanitary sewer. Crugers away and restored flow. Proklean ha | Homeowner called it in. | Less than 50 gallons were discharged into the basement. | Field estimate by crew. | No | N/A | 2022-05-17 | 11:15 PM | Less than 50 Gallons. | 50 |  | Crew jetted the line to clear the grease blockage. The crew went back the following day to clean and | East Haven | 8 Emma Rd, East Haven, CT
50
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-07-09 | 02:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Roots blocked the city main. Line was jetted and flow restored. | Homeowner called it in. | Less than 50 gallons was discharged into the basement. | Field estimate by crew. | No | N/A | 2022-07-09 | 03:30 PM | Less than 50 gallons. | 45 |  | Crew jetted the city line and restored flow. Pro Klean was contracted to clean and sanitize. | Hamden | 77 Swarthmore St, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-06-17 | 08:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Call came in from Hamden DPW for water bubbling from a MH cover. Crew jetted the line and restored f | Call came in from Hamden DPW for water bubbling from a MH cover. | Less than 30 gallons estimated by crew. | Field estimate by crew. Water was bubbling out through the pick hole in the cover. | No | N/A | 2022-06-17 | 09:15 AM | Less than 30 gallons. | 25 |  | Crew jetted the line and restored flow. the area around the MH cover was washed down. | Hamden | 314 Pine Rock Ave, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-04-13 | 03:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage in the CT Transit parking lot. The line was backed up to Edmund St. | Employee of CT Transit called it in. | less than 20 gallons. | Field estimate by crew. Sewage was exiting through the pick holes in the MH cover. It ran to the sid | No | N/A | 2022-04-13 | 04:30 PM | Less than 20 gallons. | 15 |  | Crew jetted the line in the CT Transit parking lot and cleared the line. Flow was restored and the r | Hamden | 2061 State St, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-10-17 | 08:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Crew removed grease and rags from the sanitary sewer. Crew will come back and investigate it further | Homeowner called it in. | Less than 500 gallons discharge to the basement. | 20x20x2”x7.48=496 gallons. | No | N/A | 2022-10-17 | 09:00 PM | 496 gallons | 496 |  | Crew jetted the sanitary sewer and restored flow. Pro clean was contracted to clean sanitize the bas | Hamden | 23 Eleanor St, Hamden, CT
581
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-01-06 | 02:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Rags in the sanitary system. | Resident called it in. | Less than 100 gallons were discharged to the road surface. | Field estimate by crew. | No | N/A | 2022-01-06 | 03:15 PM | Less than 100 gallons. | 95 |  | Crew jetted the sanitary sewer. | New Haven | 52-54 Victory Dr, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-01-17 | 04:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | permitted | SCADA notification | 5.1 MG | totalized flow meter | Yes | New Haven Harbor | 2022-01-17 | 11:30 AM | 5.1 MG | 5100000 |  | flows decreased | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-01-23 | 06:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | There was a mass of grease that was removed from the system down the street from the callers house. | Homeowner called it in. | Less than 20 gallons was discharged. | Field estimate by crew. | No | N/A | 2022-01-23 | 07:15 PM | Less than 20 gallons. | 19 |  | Crew jetted the line and restored flow. Pro Klean will clean and sanitize Monday morning, 1/24/22. | New Haven | 36 Spencer Pl, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-01-25 | 01:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots |  | Reported by Homeowner | 168 gallons | Field estimate by crew1.5" (.125ft) x 12 x 15 x 7.48 = 168.3 gallons | No | n/a | 2022-01-25 | 01:45 PM | 168 gallons | 168 |  | Crew jetted line and restored flow | New Haven | 37 Hemlock Rd, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-01-25 | 08:00 PM | Basement | Raw Sewage | Unknown | Sanitary sewer surcharged. The line was jetted at the intersection of Vista Ter and Fountain St. | Homeowner called it in. | Less than 1000 gallons. | Field estimate by crew. | No | N/A | 2022-01-25 | 08:45 PM | 776 gallons were discharged into the basement.2"(.166')x25'x25'x7.48= 776.05 gallons. | 776 |  | Crew jetted the sanitary sewer and restored flow. Pro Klean was contracted to clean and sanitize the | New Haven | 147 Vista Terrace, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-04 | 05:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | flow meter |  |  | Yes | New Haven Harbor | 2022-02-04 | 07:30 PM | 1.7 MG | 1700000 |  | flows decreased | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-18 | 00:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | flows over 60 mgd at facility | SCADA |  | flow meter | Yes | New Haven Harbor | 2022-02-18 | 03:30 AM | 600,000 gallons | 600000 |  | flow decreased to facility | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-02-23 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | VARIABLE | FLOW METERING | Yes | NEW HAVEN HARBOR | 2022-02-23 | 00:15 AM | <0.1 mgd | 95000 |  | increased flows at WWTF from 2/22 storm, flow decreased below 60 mdg and permitted bypass ended. | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-02-22 | 06:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Variable | Flowmetering | Yes | New Haven Harbor | 2022-02-23 | 00:00 AM | 4.7 mgd | 4700000 |  | end of reporting day, event ended on 2/23 | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-03-12 | 10:30AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2022-03-12 | 12:00 PM | 788,000 gallons | 788000 |  | flow decreased through treatment facility | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-03-23 | 02:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease caused a backup in the city line. The crew jetted the line and restored flow. Pro Klean was c | Resident called it in. | Less than 10 gallons. | Field estimate by crew. | No | N/A | 2022-03-23 | 03:00 PM | Five gallons of water was in the basement. | 5 |  | Crew jetted the city line and restored flow. The crew will clean and CCTV inspect the line 3/24/22. | New Haven | 47 Monroe St, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-03-25 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ON GOING | ON GOING | Yes | NEW HAVEN HARBOR | 2022-03-25 | 03:00 AM | 2.4 MG | 2400000 |  | decreased flow through facility | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-04-07 | 05:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-04-08 | 00:00 AM | 1,600,000 gallons | 1600000 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-04-08 | 00:00 AM | Select... | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-04-08 | 05:00 AM | 6,600,000 gallons | 6600000 |  | flow decreased | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-04-09 | 12:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2022-04-09 | 01:30 PM | 260,000 gallons | 260000 |  | flows decreased through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-04-14 | 09:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | scada | ongoing | ongoing | Yes | NEW HAVEN HARBOR | 2022-04-14 | 10:45 PM | 0.52 MG | 520000 |  | decreased flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-04-17 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor. | 2022-04-17 | 00:45 AM | .19 MG | 19000000 |  | decreased flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-04-16 | 11:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-04-17 | 00:00 AM | 0.25 MG | 250000 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-04-19 | 01:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-04-19 | 07:45 AM | 7.6626 MG | 7662600 |  | flow decreased through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-04-24 | 10:30AM | Lateral - Private | Raw Sewage | Mechanical Equipment Failure | Possible damage to private lateral causing sewage to perk up through the asphalt. This is an intermi | A resident reported it through See Click Fix. | Less than 50 gallons. This is an intermittent condition. | Field estimate by crew. There is only a wet spot in the asphalt near a repair patch in the road. It | No | Quinnipiac River | 2022-04-25 | 01:45 PM | Crew is estimating less than 50 gallons. There was no sewage coming up at the time of the GNHWPCA in | 40 |  | The GNHWPCA has hired a contractor to attempt to clear the line. This investigation is being conduct | New Haven | 88 Front St, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-05-02 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-05-02 | 07:45 PM | 0.26 MG | 260000 |  | rain ended, reduced flows at WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-05-20 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | SCADA | 140000 | SCADA | Yes | NEW HAVEN HARBOR | 2022-05-20 | 11:45 PM' | 140,000 | 140000 |  | Permitted secondary diversion | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-05-28 | 03:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2022-05-28 | 04:30 PM | 0.3682 MG | 368200 |  | flow decreased | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-06-02 | 05:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-06-02 | 06:45 PM | .7424 MG | 742400 |  | reduction in flow to facility | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-06-08 | 03:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-06-08 | 05:45 AM | 0.34 MG | 340000 |  | reduced flow through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-06-09 | 07:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-06-09 | 08:30 AM | 1.6 MD | 1600000 |  | flow decreased through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-06-22 | 08:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | scada | ongoing | ongoing | Yes | new haven harbor | 2022-06-22 | 06:45 PM | 2.43 MG | 2430000 |  | reduction of flow at the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-06-27 | 05:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | On-GOING | Yes | NEW HAVEN HARBOR | 2022-06-27 | 05:30 PM | 0.1022 MG | 102200 |  | reduced flow through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-06-28 | 05:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | The crew cleaned grease and rags from the sanitary sewer. | The property owner called it in. | Less than 50 gallons was discharged into the basement. | Field estimate by crew. | No | N/A | 2022-06-28 | 05:45 PM | Less than 50 gallons were discharged into the basement. | 45 |  | Crew jetted to sanitary sewer and restored flow. Pro Klean was contracted to clean and sanitize the | New Haven | 238 Wallace St, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-06-29 | 05:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Crew jetted the sanitary sewer and found the line to be blocked by roots. The line was cleared and f | The homeowner called the back up in. | Less than 50 gallons was visible as a discharge into the basement. | Field estimate by crew. | No | N/A | 2022-06-29 | 06:30 PM | Less than 50 gallons. | 45 |  | Crew jetted to sanitary sewer and restored flow. Pro Klean has been contracted to clean and sanitize | New Haven | 31 Fountain Terrace, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-07-18 | 11:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | high flows | scada | ongoing | ongoing | Yes | new haven harbor | 2022-07-18 | 03:00 PM | 3.88 MG | 3880000 |  | flow reduction through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-07-19 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | increased flows | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-07-19 | 01:30 AM | 0.497 MG | 497000 |  | flows reduced through the treatment facility | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-08-01 | 05:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-08-01 | 06:00 AM | 0.2377 MG | 237700 |  | flow reduction through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-08-09 | 04:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Flow meter | ongoing | flow meter | Yes | new Haven HArbor | 2022-08-09 | 04:30 PM | 0.0626 MG | 62600 |  | reduced flows through wwtp | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2022-08-22 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | New Haven Harbor | 2022-08-23 | 00:00 AM | 0.7517 MG | 751700 |  | decreased flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2022-08-23 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-08-23 | 02:15 AM | 2.7191 MG | 2719100 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-09-06 | 05:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain event 2.0" at WWTF and larger volumes experienced through the service area | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-09-06 | 09:00 PM | 19.043 MG | 19043000 |  | flows decreased through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-09-06 | 09:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | During heavy rain event several manhole covers were reportedly pushed off their frames. The covers | Missing manhole covers were called in by city agencies and residents. | Undetermined. When crews went to each location, covers were on with no discharge. | N/A | No | Undetermined, there was no discharge at the time of the inspection. | 2022-09-06 | 10:30AM | undetermined | 300 |  | Rain fall dropped off, flows dropped. | New Haven | New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-09-13 | 06:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-09-13 | 08:45 AM | 3.1522 MG | 3152200 |  | reduction of flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-09-19 | 07:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-09-19 | 08:45 PM | 0.4874 MG | 487400 |  | flows reduced through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-09-22 | 09:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOWS STORM EVENT | SCADA | ONGOING | ONGOING | Yes | New Haven Harbor | 2022-09-22 | 03:00 PM | 5.0966 | 5096600 |  | flows reduced through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-10-01 | 09:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | wet weather | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-10-01 | 09:30 AM | 0.0251 MG | 25100 |  | flows decreased through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-10-05 | 03:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-10-05 | 05:30 PM | 1.2044 MG | 1204400 |  | flows at WWTF decreased | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-10-13 | 08:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-10-13 | 09:15 PM | 0.2988 MD | 298800 |  | flow reduction through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-10-13 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | The city line was blocked with grease. The line was jetted and flow restored. | Property owner called it in. | Less than 100 gallons. | Field estimate by crew. | No | N/A | 2022-10-13 | 10:45 AM | Less than 100 gallons. | 95 |  | The GNHWPCA jetted the city line and restored flow. The line was cleaned and grease removed. Pro Kle | New Haven | 75 Whitney Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2022-10-13 | 03:00 PM | Manhole | Raw Sewage | Unknown |  | RWA reported water from a MH at the work site. | 200 gallons discharged from the MH. | Field estimate by crew. | No | N/A | 2022-10-13 | 03:45 AM | Less than 200 gallons. | 195 |  | Crew jetted the city line and restored flow. Crew cleaned out the basin. | New Haven | 39 Onyx St, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-10-14 | 01:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-10-14 | 05:45 AM | 1.1628 MG | 1162800 |  | flow decreased through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-10-24 | 08:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | scada | active | undetermined/ ongoing | Yes | new haven harbor | 2022-10-24 | 04:15 PM | 7.1579 MG | 7157900 |  | Flow decrease through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-11-11 | 06:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-11-11 | 09:15 PM | 2.1070 MG | 2107000 |  | flow decreased through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-11-15 | 11:45 PM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | UNDETERMINED / ONGOING | Yes | NEW HAVEN HARBOR | 2022-11-16 | 00:00 AM | 0.993 MG | 993000 |  |  | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-11-27 | 04:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-11-27 | 10:00 PM | 2.864 MG | 1864000 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-11-30 | 03:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-11-30 | 06:30 PM | 1.6418 MG | 1641800 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-12-03 | 11:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2022-12-03 | 03:30 PM | 2.7310 MG | 2731000 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-12-06 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-12-07 | 00:00 AM | 0.43 MG | 430000 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-12-07 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-12-07 | 11:15 AM | 15.51 MG | 15510000 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-12-07 | 10:30AM | Manhole | Raw Sewage | Unknown | Bypass occurred during a rain event. | Engineer working in the area called it in. | Less than 50 gallons | Field estimate by crew. Occurred during a rain event. | No | N/A | 2022-12-07 | 11:00 AM | Less than 50 gallons. | 45 |  | Crew jetted the line and restored flow. The crew was CCTV inspecting the line to determine the cause | New Haven | 45 Brooklawn Cir, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-12-16 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-12-16 | 02:45 PM | 0.5823 MG | 582300 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-12-15 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-12-16 | 00:00 AM | 0.8119 MG | 811900 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2022-12-23 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-12-23 | 01:45 AM | 0.5626 MG | 562600 |  | Reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2022-12-22 | 09:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2022-12-23 | 00:00 AM | 2.4194 MG | 2419400 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-12-31 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGIONG | ONGIONG | Yes | NEWHAVEN HARBOR | 2023-01-02 | 00:00 AM | 0.0014 MG | 1400 |  | reduced flows | New Haven | 345 E Shore Pkwy, New Haven, CT
132690928
These reports were removed from the count as they were anitcipated but resulted in 0 flows making them non-reportable
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-01-01 | 11:45 PM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Though the facility flow was over 60 MG, diversion gates did not open and 0 gallons of flow entered | 0 | Though the facility flow was over 60 MG, diversion gates did not open and 0 gallons of flow entered | No |  | 2022-01-01 | 01:00 PM | 0 |  |  | High flows ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-03-06 | 12:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  |  |  |  | Yes | new haven harbor | 2022-03-06 | 12:00 PM | 0 gallons |  |  | decreased flows through the treatment plant | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2022-05-07 | 09:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | No | New Haven Harbor | 2022-05-07 | 10:00 AM | 0 gallons |  |  | it didn't occur | New Haven | 354 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-08 | 02:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | flow trigger of >60.0 MGD |  |  | No | none | 2022-02-08 | 02:15 AM | 0.0 gallons |  |  | flow decreased | New Haven | 345 E Shore Pkwy, New Haven, CT

## GREENWICH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2022-03-10 | 10:30AM | Manhole | Raw Sewage | Other | Please see comments above for explanation of bypass cause. | Reported by Highway Inspector | Unknown at time of initial report - however, final estimate is provided later in this report | N/A | Yes | Byram River | 2022-03-10 | 04:15 PM | Approximately 23,000 gallons total |  | Removed failed repair coupling and installed new repair coupling. | Greenwich | 60 S Water St, Greenwich, CT
23000

## GROTON - CITY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2022-08-14 | 04:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Resident reported | 5-10 gallons | Visual. Slow/low flow | No |  | 2022-08-14 | 05:45 PM | 5-10 gallons | 9 |  | Jetting line to remove rag/grease blockage | Groton | 79 Litton Ave, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Snowmelt | 2022-01-31 | 05:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Resident reported sewage in basement to utility. | 5-10 Gallons | Visual estimate of basement | No |  | 2022-01-31 | 07:30 PM | Less than 10 gallons total | 9 |  | Jetted line, flow resumed as normal | Groton | 378 CT-349, Groton, CT
18

## GROTON - TOWN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
GROTON, TOWN OF | Closed | Sewage Bypass | Rain 2-3" per hour | 2022-09-05 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | Effluent Pump Station Electrical Failure. 3 of 4 pumps inoperative. Flow exceeded capacity of rema | SCADA | 2-3MGD rate | Scada | Yes | Fort Hill Brook to Mumford Cove | 2022-09-06 | 04:00 AM | 1.1 MG | 1100000 |  | Flow diminished | Groton | 170 Gary Ct, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-12-22 | 03:00 PM | Sewer Main | Raw Sewage | Other | Break in Sewage Force main | Water company contact after resident contact | 1 gpm | Visual | Yes | Unnamed wetland off Pons Road - (drains to Haley Brook) | 2022-12-28 | 03:30 PM | 8000 to 9000 gal | 8500 |  | excavate, repair force main | Groton | 58 Pumpkin Hill Rd, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Other | 2022-10-02 | 11:15 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | One of two pumps and pump control system failed. Electrical problem believed to be caused by high | Mission monitoring system | 1.2 cfm | visual | No |  | 2022-10-02 | 03:45 PM | Estimate 2600 gallons | 2600 |  | Portable pumps were deployed to bypass the station. Sewage bypass ended at 3:45pm. | Groton | 40 Birch St, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Dry | 2022-05-09 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Routine Inspection by WPCD personnel | 1 GPM | Visual estimate, leak was from manhole vent holes | No |  | 2022-05-09 | 03:30 PM | 15000 gallons | 15000 |  | Jetted sewer. | Groton | 170 Gary Ct, Groton, CT
1126100

## KILLINGLY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
KILLINGLY | Closed | Sewage Bypass | Dry | 2022-07-19 | 08:45 AM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | Sludge hauler was removing trailer from facility when tailgate opened dumping sludge cake on the roa | Driver from sludge hauler | 5 yds of sludge cake | Visual | No |  | 2022-07-19 | 10:00 AM | NA | 0 |  | Sludge hauler was removing trailer from facility when tailgate opened dumping sludge cake on the roa | Killingly | 31 Wauregan Rd, Killingly, CT
KILLINGLY | Closed | Sewage Bypass | Dry | 2022-07-19 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Caller identified | 100 gallons. Just started to reach catch basin. | Visual estimate | No |  | 2022-07-19 | 12:30 PM | 200 gallons | 200 |  | Septic hauler pumped down manhole and crew jetted sewer line. | Killingly | 365 Putnam Pike, Killingly, CT
KILLINGLY | Closed | Sewage Bypass | Snowmelt | 2022-02-07 | 02:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Town employee called treatment plant | 200 to 300 Gallons | Estimated | Yes | Five Mile Pond | 2022-02-07 | 03:15 PM | 200 to 300 gallons | 250 |  | Suez employees jetted line to clear blockage. Town CEO on site during incident | Killingly | 39 Prospect Ave, Killingly, CT
KILLINGLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-11-27 | 05:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Phone call | 250 gallons | Estimated | No |  | 2022-11-27 | 08:30 PM | 250 gallons | 250 |  | Manholes were paved over. Crew had to get air compressor and jack hammer. Then had to search for blocked manhole. Blockage was found at the Wal-Mart lateral manhole | Brooklyn | 450 Providence Rd, Brooklyn, CT
700

## LITCHFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
LITCHFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-12-23 | 06:15 AM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure | We lost power and the generator failed to run for some unknown reason. | Alarms call from the plant and Superintendent responding to the alarm. | Over 600 GPM but no flow meter. After we restored power the flows the flows were up to 1,300 GPM. | Visual observations and the effluent flow meter after power was restored. | Yes | Bantam River. | 2022-12-23 | 08:00 AM | 156,000 gallons, | 156000 |  | We sprayed ether into the air filter while trying to start the generator and it kicked back on. We t | Litchfield | 29 Stoddard Rd, Litchfield, CT
LITCHFIELD WPCF | Closed | Sewage Bypass | Snowmelt | 2022-02-02 | 10:45 AM | Pump Station | Raw Sewage | Electrical Equipment Failure |  | During routine pump station checks | <3 gallons | Estimated | No |  | 2022-02-02 | 11:00 AM | <3 gallons | 2 |  | The electrical component that failed has been temporarily repaired while we wait for parts. | Litchfield | 111 Wells Run, Litchfield, CT
LITCHFIELD WPCF | Closed | Sewage Bypass | Dry | 2022-11-05 | 09:00 AM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure | The hose that was secured to the railing of the septage pit because lose and the hose began sprayi | By the operator on duty who was monitoring the pumping dwn f the diversin tank | Less than 500 gallons. | Visual inspection. | Yes | Bantam River. | 2022-11-05 | 09:30 AM | Less than 500 gallons. | 450 |  | The pumped was turned off and the hose was properly secured to the railing on the tank. | Litchfield | 29 Stoddard Rd, Litchfield, CT
LITCHFIELD WPCF | Closed | Sewage Bypass | Snowmelt | 2022-02-02 | 10:45 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | The pump motor VFDs faulted out, unknown why. Causing around 3 gallons of raw sewage to overflow ou | During weekly pump station checks | 3 gallons | Estimate | No |  | 2022-02-02 | 12:00 PM | 3 gallons | 3 |  | Electrical malfunction was repaired and pump station placed back in service | Litchfield | 111 Wells Run, Litchfield, CT
156455

## MANCHESTER
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2022-03-16 | 06:00 PM | Treatment Plant | Sludge Spill | Other | During cleaning of our tank the vac truck was dumping at the septage dumping station and the sump go | observation | 200 gallons | observation | No |  | 2022-03-16 | 08:00 PM | 200 gallons |  | During cleaning of our tank the vac truck was dumping at the septage dumping station and the sump go | Manchester | 120 Thrall Rd, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2022-04-05 | 11:45 PM' | Treatment Plant | Sludge Spill | Electrical Equipment Failure | The level indicator for the thickened sludge tank was not reading properly and the tank overflowed. | operator observation | 100 gallons | operator estimate | No |  | 2022-04-05 | 12:00 PM | 100 gallons |  | The operator cleaned the transducer and we created a redundant circuit to go with the highest readin | Manchester | 120 Thrall Rd, Manchester, CT
300

## MATTABASSETT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-04-08 | 08:45 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | New Britain flows hit 38 MGD with heavy rain. Middletown hit 11 MGD with heavy rain. | Operator opened bypass gate | 13 MGD at time of bypass gate opening. | Difference between influent and effluent parshall flumes. | Yes | Connecticut River | 2022-04-09 | 00:00 AM | 2,433,645 gallons of partially treated effluent we combined with 34,947,916 gallons of fully treated |  | When plant flows subsided under 55 MGD we closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
2433645

## HARTFORD - MDC
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimate | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-07-19 | 12:30 PM | Basement | Raw Sewage | Unknown | DEBRIS IN M/S | PLUMBER | <100 GALLONS | MDC CLAIMS AGENT | No |  | 2022-07-19 | 01:00 PM | <1000 GALLONS | 95 |  | MDC JET TRUCK RELIEVED M/S | Bloomfield | 6 Pasture Ln, Bloomfield, CT
95
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimate | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-10-27 | 02:00 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | Leak on Force Main | MDC PERSONNEL | <100g | MDC PERSONNEL | Yes | Ct River | 2022-10-27 | 08:00 PM | <1000g | 975 |  | MDC FORCES REPAIRED FORCE MAIN & CLEANED AREA | East Hartford | 160 Governor St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-10-18 | 02:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Soft Stoppage - Paper, etc. | BUILDING OWNER REPORTED | <100g | MDC PERSONEL | No |  | 2022-10-18 | 03:15 PM | <100gal | 95 |  | Jet truck relieved soft stoppage in M/S | East Hartford | 50 Chapman Pl, East Hartford, CT
1070
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimate | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-05-28 | 10:15 AM | Basement | Raw Sewage | Mechanical Equipment Failure | Sewer main collapsed | Reported by plumbing contractor | <100gals | MDC personnel | No |  | 2022-05-28 | 04:30 PM | 10 Gallons | 10 |  | Repaired the collapsed sewer main | Hartford | 80 Jefferson St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-06-07 | 07:15 PM | Manhole | Raw Sewage | Unknown |  | MDC PERSONNEL | <100gals | MDC Personnel | No |  | 2022-06-07 | 08:30 PM | <100G | 95 |  | MDC CREWS MAKING REPAIRS | Hartford | 195 Columbus Blvd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-11-10 | 11:15 AM | Manhole | Raw Sewage | Other | CONTRACTOR WAS PERFORMING A BYPASS | MDC SCADA SYSTEM | 7000g | MDC SCADA SYSTEM | Yes | SOUTH BRANCH PARK RIVER | 2022-11-10 | 12:00 PM | 7000g | 7000 |  | CONTRACTOR MODIFIED BYPASS PUMPING | Hartford | 31 Wilson St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-04-11 | 01:30 PM | Manhole | Raw Sewage | Unknown | DEBRIS | PASSER BY | < 100G | MDC PERSONELL | Yes | CT RIVER | 2022-04-11 | 02:15 PM | <100G | 95 |  | JET TRUCK RELIEVED M/S | Hartford | 195 Columbus Blvd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-10-28 | 07:45 PM | Manhole | Raw Sewage | Unknown | DEBRIS IN M/S | HARTFORD POLICE | <100G | MDC CLAIMS AGENT | No |  | 2022-10-28 | 09:30 AM | <100 gallons | 95 |  | MDC CREW RELIEVED M/S WITH JET TRUCK | Hartford | 14 Haynes St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-05-28 | 04:30 PM | Sewer Main | Raw Sewage | Other | sewer repair due to sewer collapse | CCTV | to be determined | mdc personnel | No |  | 2022-05-29 | 00:45 AM | 25,200 Gallons | 25200 |  | Repaired Sewer main | Hartford | 80 Jefferson St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-02-10 | 03:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | GREASE & ROOTS | REPORTED BY UNIVERSITY OF HTFD | < 100g | MDC CREW LEADER | Yes | LOCAL WATERCOURSE (STREAM) | 2022-02-10 | 03:45 PM | < 100g | 95 |  | MDC JET TRUCK RELIEVED M/S | Hartford | Alfred C. Fuller Music Center, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-03-10 | 12:45 PM | Manhole | Raw Sewage | Excessive Flows - Snow Melt |  | MDC SCADA SYSTEM | 20000g | MDC SCADA SYSTEM | Yes | PARK RIVER CONDUIT | 2022-03-10 | 01:30 PM | 20,000g | 20000 |  | EVENT DUE TO SNOW MELT - SNOW MELTED | Hartford | 452 Broad St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-02-13 | 03:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | CUSTOMER CALLED HAVING SEWAGE BACK UP IN BASEMENT | LESS THAN 100 GAL | MDC PERSONNEL | No |  | 2022-02-13 | 05:30 PM | LESS THAN 100 GALLONS | 95 |  | MDC SEWER CREW JETTED MAIN LINE AND RELIEVED BLOCKAGE | Hartford | 85 Van Block Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-02-13 | 01:00 AM | Manhole | Raw Sewage | Other | EXCESSIVE FLOW DUE TO WATER MAIN BREAK | MDC SCADA SYSTEM | 1000 GAL | MDC SCADA | Yes | SOUTH BRANCH PARK RIVER | 2022-02-13 | 01:45 AM | 2000 GAL | 2000 |  | ONCE WATER MAIN WAS SHUT DOWN EXCESSIVE FLOWS RECEDED AND BYPASS STOPPED | Hartford | 52 Wilson St, Hartford, CT
54685
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimate | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-06-03 | 12:30 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | Break in Force Main from Station | MDC employee | <100g | MDC Visual | No |  | 2022-06-03 | 04:15 PM | <100g | 95 |  | MDC FORCES MADE REPAIRS | Newington | 200 Old Farm Dr, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-09-06 | 11:45 AM' | Manhole | Raw Sewage | Excessive Flows - Storm Event | OVERFLOW DUE TO RAIN EVENT | MDC SCADA SYSTEM | <1000g | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2022-09-06 | 07:15 PM | 0.009mg | 9000 |  | RAIN EVENT ENDED - FLOWS RECEDED | Newington | 711 N Mountain Rd, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-09-08 | 08:30 PM | Basement | Raw Sewage | Unknown | GREASE | PLUMBER | <100 GALLONS | MDC PERSONNEL | No |  | 2022-09-08 | 10:15 PM | <1000 | 95 |  | MDC JET TRUCKED RELIEVED M/S | Newington | 105 Fisk Dr, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-04 | 06:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT | MDC SCADA SYSTEM | 0.018MG | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2022-02-04 | 10:00 PM | 1.340 MG | 1340000 |  | STORM EVENT ENDED AND EXCESSIVE FLOWS RECEDED | Newington | 711 N Mountain Rd, Newington, CT
1349190
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimate | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-08-05 | 07:00 AM | Sewer Main | Raw Sewage | Other | sewer repair due to sewer lining failure | CCTV | TBD | MDC PERSONNEL | No |  | 2022-08-11 | 03:45 PM | 0 | 0 |  | REPAIR MAIN SEWER | West Hartford | N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-22 | 11:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | 0.038 MG | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2022-02-23 | 00:30 AM | 0.065mg | 65000 |  | WET WEATHER ENDED. FLOWS DROPPED BELOW OVERFLOWS | West Hartford | 123 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-19 | 00:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Main Sewer Surcharged | Home owner reported. | <100g | Home owner | No |  | 2022-04-19 | 12:00 PM | <100g | 95 |  | Surcharged event has ended | West Hartford | 186 N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-03-25 | 02:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT | MDC SCADA | LESS THAN 1000 GAL | MDC SCADA | Yes | PIPER BROOK | 2022-03-25 | 10:45 PM | 0.137mg | 137000 |  | STORM EVENT ENDED | West Hartford | 67 Southwood Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-07-02 | 12:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | plumber | < 5 gals | mdc personnel visual | No |  | 2022-07-02 | 01:45 PM | <5 gals | 5 |  | main sewer cleared of blockage | West Hartford | 76 Berkshire Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-02-16 | 03:30 PM | Basement | Raw Sewage | Unknown | SOFT STOPPAGE IN M/S | PROPERTY OWNER | < 100g | MDC PERSONNEL | No |  | 2022-02-16 | 04:45 PM | <100g | 95 |  | JET TRUCK RELIEVED M/S | West Hartford | 8 Sims Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-04-08 | 09:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT - SURCHARING SEWER | RESIDENT | 100g | MDC PERSONELL | Yes | TROUT BROOK RIVER | 2022-04-08 | 02:15 PM | 100g - 1000g | 950 |  | FLOW LEVELS RECEEDED | West Hartford | 215 Ballard Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-06-02 | 09:45 PM | Basement | Raw Sewage | Unknown | OUTSIDE CONTRACTOR DAMAGE | MDC PERSONELL | 100 - 1000G | MDC PERSONELL | No |  | 2022-06-03 | 04:30 AM | 100-1000G | 950 |  | CLEANING OF M/S - REPAIRS TO M/S | West Hartford | 95 St Augustine St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-08 | 03:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1,000 GALLONS | MDC SCADA | Yes | TROUT BROOK | 2022-04-08 | 06:00 AM | 11,000 GALLONS | 11000 |  | EXCESSIVE FLOWS RECEDED ONCE WET WEATHER EVENT ENDED | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-04-05 | 10:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | M/S backed up due to roots | Homeowner | <100 | MDC PERSONELL | No |  | 2022-04-06 | 00:45 AM | <100 Gallons | 95 |  | MDC sewer flushed by jet truck and stoppage relieved | West Hartford | 35 Lostbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-08 | 01:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1,000 GALLONS | MDC SCADA | Yes | TROUT BROOK | 2022-04-08 | 02:00 PM | 2.697MG | 2697000 |  | EXCESSIVE FLOWS RECEDED ONCE WET WEATHER EVENT ENDED | West Hartford | 109 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-04-05 | 10:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | M/S BACKED | HOMEOWNER | <100G | MDC PERSONELL | No |  | 2022-04-06 | 00:45 AM | <100G | 95 |  | JET TRUCK RELIEVED M/S | West Hartford | 35 Lostbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-08 | 01:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 9.2 MG | MDC SCADA | Yes | PIPER BROOK | 2022-04-10 | 00:45 AM | 9.2 MG | 9200000 |  | RAIN EVENT ENDED EXCESSIVE FLOWS RECEDED | West Hartford | 17 Steven St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-11-10 | 12:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | HOMEOWNER | <100 GALLONS | MDC EMPLOYEE | No |  | 2022-11-10 | 01:30 PM | < Then a 1000 Gallons | 950 |  | Sewer Dept jetted the main sewer until blockage was relieved | West Hartford | 1150 New Britain Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-11-20 | 11:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | CALLED IN BY PLUMBER | <100G | MDC PERSONNEL | No |  | 2022-11-20 | 02:00 PM | Less than 10 Gals | 9 |  | Sewer main cleared by jet truck of obstruction/grease | West Hartford | 38 Iroquois Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-10 | 10:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | < 1000 GALLONS | MDC PERSONNEL | No |  | 2022-04-10 | 10:45 AM | < 1000 GALLONS | 950 |  | High flow receded. | West Hartford | 1 Fox Meadow Ln, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-19 | 04:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | <1,000 | MDC SCADA | Yes | TROUT BROOK | 2022-04-19 | 09:45 AM | 0.535mg | 535000 |  | EXCESSIVE FLOWS RECEDED ONCE WET WEATHER EVENT ENDED | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-19 | 04:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | >1000,000 | MDC SCADA | Yes | PIPER BROOK | 2022-04-20 | 00:30 AM | 4.271MG | 4270000 |  | EXCESSIVE FLOWS RECEDED ONCE WET WEATHER EVENT ENDED | West Hartford | Hillcrest Ave, West Hartford, CT
16919194
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2022-03-18 | 11:00 AM | Lateral - Private | Raw Sewage | Unknown | Issue with house lateral | Private property issue reported to MDC | <100g | Visual | Yes | Farmington River | 2022-03-18 | 12:00 PM | <100g | 95 |  | Private Lateral pipe was repaired and relieved - event has ended. | Windsor | 351 Broad St, Windsor, CT

## MERIDEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
MERIDEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-03-24 | 10:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | Manhole is located in a ROW in the woods near a linear trail. | BY a resident walking the Quinnipiac River Linear trail | 50-100 gallons escaped | Visual estimation | Yes | Quinnipiac River | 2022-03-24 | 11:00 AM | Approx 50-100 gallons | 95 |  | Upon arrival WPCF staff used their Jetter truck to break the blockage. once normal flow resumed staf | Meriden | 201 River Rd, Meriden, CT
95
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
MERIDEN | Closed | Sewage Bypass | Dry | 2022-07-11 | 12:15 PM | Lateral - Private | Raw Sewage | Other | Private sewer lateral that runs under a pedestrian walkway rotted and started to leak into Harbor Br | Call was placed to the Meriden WPCF to check on water coming out of a pipe by a passerby. | approx 40 gpm. | visual determination | Yes | Harbor Brook | 2022-07-11 | 06:00 PM | Approx 8,000 gals. Main flow was slowed down to a trickle by about 2:00 PM and completely stopped by | 8000 |  | Building owner called in a plumbing company to remove and replace the rotted piece of sewer pipe wit | Meriden | 80 Hanover St, Meriden, CT

## MIDDLETOWN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
MIDDLETOWN WPCA | Closed | Sewage Bypass | Dry | 2022-09-27 | 07:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | construction work caused manhole to get partially pushed over and dabre fell in causing a blockage | called in by resident | 2,000 gallons | visual | No |  | 2022-09-28 | 01:15 PM | 2,000 gal |  | removed roots from manhole structure | Middletown | 565 Newfield St, Middletown, CT
2000

## MILFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2022-07-03 | 12:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | A rubber gasket material and 6" PVC pipe caused the blockage. Possibly from shoddy construction. | Call from resident | 500 gal | estimate | No |  | 2022-07-03 | 05:00 PM | 500 gal | 500 |  | cut and removed rubber gasket and jet-rodded main. Will follow up with CCTV inspection. | Milford | Gulf St, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2022-03-25 | 01:00 PM | Basement | Raw Sewage | Unknown | Cleared a soft blockage but could not identify what it was. | phone call from resident | 50 gal | estimate | No |  | 2022-03-25 | 03:00 PM | 50 gallons | 50 |  | cleared blockage with jetter. | Milford | 29 Ingersol Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2022-03-30 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | Call from Regional Water | 100 | estimate | No |  | 2022-03-30 | 12:00 PM | 100 | 100 |  | Septic truck to dewater manhole and then remove roots | Milford | 417 Woodmont Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2022-08-28 | 06:00 AM | Treatment Plant | Sludge Spill | Sewage Line Blockage - Other | 8" overflow pipes failed to drain excess sludge from the sludge storage tanks. | Operator on weekend rounds | 4000 gallons | estimate | No | NA | 2022-08-28 | 08:30 PM | 4000 gallons | 4000 |  | Raw Sludge pump was shut down to prevent any additional sludge entering the overflowing tank. Sludg | Milford | 1225 Oronoque Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2022-03-25 | 01:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Soft blockage. CCTV did not reveal any obvious defects. | homeowner | 1-50 gal | estimate | No |  | 2022-03-25 | 03:00 AM | 50 | 50 |  | jetted to clear line. Did not see any material that could have caused blockage. CCTV did not revea | Milford | 29 Ingersol Rd, Milford, CT
4700

## MONTVILLE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimaton | How was Final Volume Determined | How incident was resolved | Municipality | Address
MONTVILLE | Closed | Sewage Bypass | Dry | 2022-03-22 | 11:45 AM' | Treatment Plant | Sludge Spill | Mechanical Equipment Failure | Gasket failure at SBR-1 discharge pipe leading to disinfection chamber. | Many observations of each of six SBRs to determine where MLSS escape was occurring. | 500 gallons | estimated based on direct observations | No |  | 2022-03-22 | 01:30 PM | 500 gallons to chlorine chamber | 500 |  | MLSS wasting increased to lower blanket level. Polymer addition to lower blanket level. No more so | Montville | 83 Pink Row, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2022-08-12 | 10:00 AM | Lateral - Private | Raw Sewage | Other | Treated WPCF Effluent is recycle via a 12-inch cast iron pipe 2 miles to RWCB facility. | Reported to PW Dept from car driver | 500 gallons of treated effluent (recycle) water | visual inspection of release location | No | n/a | 2022-08-12 | 03:00 PM | 500 g of treated effluent (used for recycle water). | 500 |  | yes. repairs completed. | Montville | 106 Maple Ave, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2022-08-12 | 00:00 AM | Lateral - Private | Disinfected Partially Treated Raw Sewage | Mechanical Equipment Failure | Treated effluent (recycle water) to RWCB line break due to poor bedding- piece of asphalt broke into | Call into Public Works at 10 a.m. | 500 g - slow seep to road surface. | Estimated time and slow seep observed. | No | n/a | 2022-08-12 | 10:30AM | 500 g | 500 |  | Repair by contracted (licensed) contractor for RWCB. | Montville | 106 Maple Ave, Montville, CT
1500

## NAUGATUCK
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
NAUGATUCK WPCF | Closed | Sewage Bypass | Snowmelt | 2022-01-28 | 09:00 AM | Sewer Main | Raw Sewage | Other | Broken force main from pump station | A town resident called it in | Possibly 50-100 gallons | Visually estimating the rate of flow over one minute | No |  | 2022-01-28 | 10:30AM | less than 100 gallons | 95 |  | Force main was repaired by outside contractor | Naugatuck | 360 Maple Hill Rd, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2022-09-26 | 06:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Rags collected at the top of a drop down. | Home owner called in the problem. | Under 100 gallons. | It only filled a washer and some on the floor. | No |  | 2022-09-26 | 07:45 PM | less than 100 gal | 95 |  | cleared rags that caused the blockage | Naugatuck | 14 Brennan St, Naugatuck, CT
190

## NEW HARTFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW HARTFORD | Closed | Sewage Bypass | Dry | 2022-10-02 | 01:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | sewer main blocked by buildup of rags | owner of the property on 17 High st noticed sewage coming from man hole. | 2 gallons a min | by eye | Yes | East Mountain Brook/ Hallock Brook | 2022-10-02 | 04:00 PM | an estimated volume. i would have to say the sewage coming out of man hole cover was about 2 gallons | 360 |  | sewer main was jetted by American Rooter to clear blockage. | New Hartford | 17 High St, New Hartford, CT
[18 empty] | 360 | 3 hours @ 2gpm?

## NEW LONDON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2022-08-30 | 09:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Roots |  | Called in by resident. | No quantity has been estimated at this time. | N/A | No |  | 2022-08-30 | 11:30 AM | Not estimated. | 45 |  | Jet rodding of sewer main. Once clog was freed the majority of the sewage in the basement was pumped | New London | 16 Cedar Grove Ave, New London, CT
45

## NEW MILFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW MILFORD | Closed | Sewage Bypass | Dry | 2022-02-10 | 12:45 PM | Select... | Raw Sewage | Sewage Line Blockage - Roots |  | Public Works official called WPCA Office and reported water leaking from sewer cleanout. | .69 GALS PER MINUTE | BY a visual of the quantity of water trickling out of cleanout. | No |  | 2022-02-10 | 03:15 PM | 103.5 Gals. | 103 |  | High Pressure jetting and a mechanical pipe cleaner. A large mass of roots was removed. The area is | New Milford | 9 Terrace Pl Ext, New Milford, CT
NEW MILFORD | Closed | Sewage Bypass | Dry | 2022-08-06 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Police Department dispatched Sewer Department. | 50-100 gallons | Estimated. | Yes | Housatonic River | 2022-08-06 | 04:00 PM | 50-100 gallons | 90 |  | When crew arrived, invert in manhole was flowing well, crew ran water jet up and down line to be sur | New Milford | 19 Bridge St, New Milford, CT
193

## NORFOLK
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORFOLK SEWER DISTRICT | Closed | Sewage Bypass | Dry | 2022-11-05 | 09:00 AM | Treatment Plant | Raw Sewage | Other | Truck Accident | Fire Call | 100,000 gallons | Flow Meter | No | N/A | 2022-11-14 | 09:00 AM | 100000 |  | No impact to water or the facility. Bypass was ceased and normal plant function resumed. | Norfolk | Norfolk, CT
100000
This bypass was precautionary to protect the treatment plant biology due to a fuel oil spill.

## NORWALK
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-03-30 | 12:30 PM | Pump Station | Raw Sewage | Other | Vactor truck failure at pump station | By truck operators | 10 gal | Not known | No |  | 2022-03-30 | 12:45 PM | Aprox 10 Gallons | 10 |  | Vac crew cleaned up spill | Norwalk | 38 S Beach Dr, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-04-03 | 11:00 AM | Treatment Plant | Raw Sewage | Other | gravity thickener overflow. The pump did not shut off automattically. We are inspecting and reapairi | by operator | Less than 500 gallons | Based on amount recovered in vac truck. | No |  | 2022-04-03 | 11:00 AM | Less than 500 gallons | 450 |  | Grass area was cleaned and and spillage was sucked up in our vac truck and disposed of in septage re | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-06-15 | 01:30 PM | Sewer Main | Raw Sewage | Other |  | call in | to be determined | to be determined | Yes | LIS | 2022-06-15 | 03:30 PM | The release lasted two hours and eleven minutes with an approximate discharge of 100 gallons perminu | 100 |  | Force main was repaired. | Norwalk | 257 Strawberry Hill Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-07-16 | 01:30 PM | Treatment Plant | Raw Sewage | Other | Septic Truck Operator was unloading and not monitoring the operation, the bar screen was clogged and raw septic waste overflowed into driveway and reached the catch basins at the Norwalk Septage Receiving Station. | Plant Operator was passing by and observed sewage spilling from the station containment area and imm | Under 1,000 Gallons | Septic tanker contained 2250 gallons before unloading, more than half the load was still in the truc | No |  | 2022-07-16 | 01:30 PM | Under 500 gallons | 450 |  | Was cleaned and disposed of properly. | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-08-26 | 08:00 PM | Select... | Raw Sewage | Other | Leave pump valve broke on bypass pump. | On site staff | 1.5 Gallons | Amount recovered in vac truck | No |  | 2022-08-26 | 09:00 PM | 1.5 Gallons | 1 |  | What was done to prevent this from happening again: Midstream blowoff valve will be shut off for the | Norwalk | 219 East Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-11-28 | 03:15 PM | Treatment Plant | Sludge Spill | Other | Driver forgot to disconnect discharge hose from septic truck. | Driver noticed quickly but had spilled some septage from hose outside containment. | 20 | Visual | No |  | 2022-11-28 | 12:00 PM | 20 | 20 |  |  | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-03-10 | 11:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | Grease, rags, and roots | Homeowner had a backup in his basement | Unknow, Happened inside owners dwelling | N/A | No |  | 2022-03-10 | 11:30 AM |  | 25 |  |  | Norwalk | 2 Reboda Ct, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-01-24 | 12:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Roots, rags, and grease | The resident at 175 Ponus Ave called the city service line. | Roughly 10 Gallons | Visual inspection on-site | No |  | 2022-01-24 | 01:00 PM | Under 50 gallons | 45 |  | Line was cleaned and vacuumed, flow was fully restore. | Norwalk | 30 Douglas Dr, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-04-12 | 04:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Found bricks in the manhole along with paper products and solids | got call from sewer crew | 20 gallons | visual observation | Yes | Unknown/No named water course in the area | 2022-04-12 | 04:45 PM | Less than 50 gallons | 45 |  | Collections team cleared and cleaned line with jet/vac truck | Norwalk | #5 Blue Mountain Rd, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-03-16 | 12:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags |  | call in by call Center | 50 gal | Visual | No |  | 2022-03-16 | 02:30 PM | 50 gal | 50 |  | Lateral was repaired. SUEZ, WPCA, and DMV work closely together to get this completed. | Norwalk | 540 Main Ave, Norwalk, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2022-11-04 | 10:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Customer Call | 1500 Gallons | Visual estimate | No |  | 2022-11-04 | 11:30 AM | 1500 Gallons | 1500 |  | Jetted man and moved rags out of invert | Norwich | 14 North St, Norwich, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-10-17 | 12:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | the owner called it in | 10 gals | unknown at this time | No |  | 2022-10-17 | 12:30 PM | Less than 10 gallons | 9 |  | Area was cleaned and flow was restored. | Norwalk | 6 Newfield St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-08-10 | 09:00 AM | Manhole | Raw Sewage | Unknown | Crew is onsite cleaning the line, will update cause when known. | Daily pump station inspection. | Less than 100 Gallons contained to asphalt | Visual | No |  | 2022-08-10 | 11:00 AM | Under 100 gallons | 95 |  | Roots removed, line cleaned and CCTVed. | Norwalk | 13 Branford St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-09-27 | 05:15 PM | Manhole | Raw Sewage | Unknown |  | Person called the Norwalk waste water treatment plant | under 100 gallons | Sewer maintenence worker at location | No | This spill reached a catch basin but the basin was dry and no flow left the basin to a waterway. |  |  | Under 100 gallons | 95 |  |  | Norwalk | 250 Westport Ave, Norwalk, CT
2895
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-03-08 | 12:15 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Collapsed Lateral | Resident saw swage coming up from ground and contacted the City | Greater than 500 Gal | To be determined | Yes | Indinan Creek off strawberry hill ave. | 2022-03-08 | 12:15 PM | Private Line |  |  | Owner had a contractor take care of it | Norwalk | 243 Strawberry Hill Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-02-24 | 12:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Private sewer lateral backed upped causing private manhole to surcharge and overflow onto private pa | Notified by 1st district water City of Norwalk | Greater than 50 gallons les than 100 gals | Visual | No |  | 2022-02-24 | 01:30 PM | Less than 100 gallons | 95 |  | Property Owner hired a contractor to clear blockage. | Norwalk | 404 Westport Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-03-23 | 07:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown blockage at this time. | Homeowner called city to inspect mainline. Our line was flowing normal. | 3 gallons | Visual | No |  | 2022-03-23 | 08:00 PM | 2-3 gallons |  |  | The Homeowner had a contractor come and clear the private lateral blockage | Norwalk | 15 Catherine St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-06-18 | 08:45 PM | Lateral - Private | Raw Sewage | Other | Caused by digging from Eversource electric company | Received call from homeowner at address | 1 to 10 gallons per hour | visual observation | No |  | 2022-06-19 | 04:00 PM | Under 500 gallons Eversource ruptured a private lateral to a building. They repaired it ASAP |  |  | Eversource and their contractor took care of the issue. | Norwalk | 24 Avenue D, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-06-28 | 02:15 PM | Lateral - Private | Raw Sewage | Unknown | Private Lateral, We do not service them, Home owner had it repaired | customer called in | less than 500 gallons | unknown | No |  | 2022-06-28 | 05:00 PM | Under 500 gallons, contained to the yard and driveway area of homeowner |  |  | Homeowner had a contractor repair their lateral. | Norwalk | 25 Soundview Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2022-03-15 | 11:45 AM' | Lateral - Private | Raw Sewage | Unknown | Was a private lateral, the city does not handle them. | Norwalk DPW |  |  | No |  | 2022-03-15 | 02:00 PM |  |  |  | Norwalk Health Dept took over and resident has repaired their lateral. | Norwalk | 52 Hill St, Norwalk, CT

## NORWICH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-22 | 07:30 PM | Manhole | Raw Sewage | Unknown |  | Customer Call | 30gpm | Visual Estimate | Yes | Shetucket River | 2022-02-22 | 08:30 PM | 1800 Gallons | 1800 |  | Jetted main and cleared blockage | Norwich | 5 8th St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2022-11-04 | 10:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Customer Call | 1500 Gallons | Visual estimate | No |  | 2022-11-04 | 11:30 AM | 1500 Gallons | 1500 |  | Jetted man and moved rags out of invert | Norwich | 14 North St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2022-12-06 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Excessive rags | customer call | 1 gpm- flowing into combined catch basin | Visual estimate | No |  | 2022-12-06 | 04:45 PM | 0 | 0 |  | Jet main, clean rags | Norwich | 65 Spruce St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2022-02-21 | 01:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags |  | Resident Called it in | 100 gallons | Visual estimate | No |  | 2022-02-21 | 02:15 PM | 100 gallons | 100 |  | Jetted line to remove blockage | Norwich | 61 Henry St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2022-09-02 | 06:00 PM | Pump Station | Raw Sewage | Electrical Equipment Failure | Breaker failure when switching back to street power from generation. | CSO alert | 18630 | flow meter | Yes | Thames River | 2022-09-02 | 07:00 PM | 18630 | 18630 |  | Reset breaker on site | Norwich | 190 S Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-09-06 | 08:30 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | Air relief on temporary bypass spitting | Customer call | Less than a gallon | visual | No |  | 2022-09-06 | 08:45 PM | 1 gallon | 1 |  | closed air relief | Norwich | 190 S Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2022-03-28 | 08:30 AM | Manhole | Raw Sewage | Mechanical Equipment Failure | Pump failed to pump when put back into service due to rotten pump base. | Flow Meter alert | 2289 Gallons | CSO Flow Meter | Yes | Thames River | 2022-03-28 | 08:45 AM | 2289 | 2289 |  | Switched back to working pump. | Norwich | 190 S Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2022-03-15 | 10:15 AM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | While installing rebuilt pump into the station, it was found that the driveshaft was knocked out of | Flow Meter alert | 1498 | CSO flow meter | Yes | Thames River | 2022-03-15 | 10:30AM | 1498 | 1498 |  | Other pump was turned on. | Norwich | 190 S Thames St, Norwich, CT
25818

## ORANGE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
ORANGE | Closed | Sewage Bypass | Dry | 2022-08-03 | 10:00 AM | Sewer Main | Raw Sewage | Other | Broken forced main | Contractor arrived at pump station to perform work and saw a sink hole developing in road | 1000 gallons | shallow sink hole and pump station does not produce much flow | No |  | 2022-08-03 | 11:30 AM | 300 |  | FORCE MAIN WAS REPAIRED | Orange | 2 Executive Blvd, Orange, CT
300

## PLAINFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2022-04-12 | 05:00 AM | Sewer Main | Raw Sewage | Other | sewer force main crack or break | resident reported water seeping out of road | about 0.5 gallons/minute | estimation using visual | Yes | Moosup River | 2022-04-14 | 11:30 AM | approximately 1800 gallons | 1800 |  | repaired sewer force main with 8" full circle repair clamp. | Plainfield | 284 Main St, Plainfield, CT
1800
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2022-06-19 | 09:30 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | sewer pumps lost prime | operator routine check | 70,000-250,000 gallons | estimation. used previous and post days flows and approximated number of hours pumps stopped pumping | No |  | 2022-06-20 | 06:30 AM | 70,000- 250,000 gallons | 150000 |  | pumps were primed and back online | Plainfield | 68 Community Ave, Plainfield, CT
150000
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2022-05-16 | 09:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | private lateral has sewer blockage. cause of blockage is unknown. | town employee notified by road workers | 300 gallons | estimation | No |  | 2022-07-27 | 10:00 AM | 300 gallons |  |  | homeowner called plumber to relieve blockage from private lateral. | Plainfield | 2 Winsor Ave, Plainfield, CT

## PLYMOUTH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2022-11-29 | 02:00 PM | Sewer Main | Raw Sewage | Other | Sewer main was broke by construction company | Construction workers discovered and called WPCA | less then 200 gallons | amount of time before break was bypassed and approximate flow | No |  | 2022-11-29 | 03:00 PM | less than 200 gallons | 190 |  | WPCA brought supplies to contractor and they made the repair to the sewer line. Line was repaired wi | Plymouth | 3 Cedar St, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2022-03-05 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Unknown- possible roots/grease in sewer Right of Way. Some grease and grit was removed during cleari | Homeowner called in. We received call from local police dispatch. | 450 gallons | It appeared to be about 5gpm from from MH and blockage was cleared approximately 1.5 hours from init | Yes | unknown. Overflow traveled across road and entered storm drain roughly 50" from MH | 2022-03-05 | 12:00 PM | 450 gallons | 450 |  | Blockage in sewer line was cleared with sewer jet truck. Line section was cleaned again of any remai | Plymouth | 14 Ronald Rd, Plymouth, CT
640
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2022-04-25 | 08:30 AM | Lateral - Private | Raw Sewage | Other | Damage to residents lateral during installation of Gas main | Homeowner called the Plymouth WPCF | Very little trickling onto road. Less than 5 gallons | Observed a wet area on the road but nothing spilling at the time of inspection | No |  | 2022-04-25 | 10:15 AM | Less then 5 gallons | 4 |  | It was a private property issue. Homeowner contact someone to repair. | Plymouth | 8 Walnut St, Plymouth, CT

## PUTNAM
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
PUTNAM | Closed | Sewage Bypass | Dry | 2022-01-03 | 10:30AM | Sewer Main | Raw Sewage | Other | forced sewer main break | wpca employee | 100 gallons | visual estimation | No |  | 2022-01-03 | 12:30 | 100 | visual estimation |  | Putnam | 83 Park Rd, Putnam, CT
100

## RIDGEFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
RIDGEFIELD (RT7), TOWN OF | Closed | Sewage Bypass | Dry | 2022-07-27 | 12:30 PM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure | Supernatant pump failure | On duty operator noticed water coming out tank. | Approximately 25 Gallons | Visual estimate and duration of water coming out of tank. | No |  | 2022-07-27 | 12:45 PM | Approximately 25 gallons | 25 |  | Area around supernatant tank was cleaned, and new on/off float installed for pump. | Ridgefield | 871 Ethan Allen Hwy, Ridgefield, CT
25
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2022-12-08 | 05:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage | Called in by restaurant owner | <200 gallons | Visual estimate and duration | No |  | 2022-12-22 | 01:45 PM | <200 gallons | 190 |  | cleared blockage with our vactor truck. | Ridgefield | 20 West Ln, Ridgefield, CT
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2022-04-21 | 11:45 AM' | Pump Station | Raw Sewage | Electrical Equipment Failure | Bubbler system stopped working due to air compressor failure. | Operator discovered during routine operational inspection. | <100 gallons | By visual estimate and duration. | Yes | Great swamp. | 2022-04-21 | 12:00 PM | <100 gallons | 90 |  | Replaced faulty air compressor with a new compressor. | Ridgefield | 120 Prospect St, Ridgefield, CT
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2022-12-08 | 05:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | Sewer lateral had grease in it, building owner had lateral cleaned which caused grease blockage in m | Called in by building owner. | <200 gallons | Visual estimate and duration. | No |  | 2022-12-08 | 07:00 PM | <200 gallons | 190 |  | Building owner had private lateral cleaned while we cleaned main line in front of building. | Ridgefield | 20 West Ln, Ridgefield, CT
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2022-04-21 | 10:00 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | Bubbler stopped working due to air compressor failure. | Operator discovered during routine operational inspection. | <100 gallons | By visual estimate and duration. | Yes | Great Swamp | 2022-04-25 | 12:00 PM | <100 gallons | 90 |  | Operator noticed pump station wet well had a small amount of water trickling out. Put pumps into man | Ridgefield | 120 Prospect St, Ridgefield, CT
560

## SEYMOUR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
SEYMOUR WPCF, TOWN OF | Closed | Sewage Bypass | Dry | 2022-05-19 | 10:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Manhole invert plugged up at manhole exit pipe with a lot of paper products/rags | Police Station called that the police station basement had sewage coming up the floor drains. | 25-30 gallons | quantity of sewage on parts of basemnt floor | No |  | 2022-05-18 | 11:00 AM | 30 gallons | 30 |  | Blockage in pipe was jetted and pipe was cleaned.Basement was cleaned up, sanitized and deodorized b | Seymour | 11 Franklin St, Seymour, CT
SEYMOUR WPCF, TOWN OF | Closed | Sewage Bypass | Dry | 2022-06-19 | 05:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Combination of Roots and Rags | Homeowner | 300 gallons | Amount of sewage pumped from basement | No |  | 2022-06-19 | 11:15 AM | 300 gallons | 300 |  | WPCF Staff Jetted sewer line from downstream manhole. Removed a root mass and rags. Clean up company | Seymour | 91 Walnut St, Seymour, CT
SEYMOUR WPCF, TOWN OF | Closed | Sewage Bypass | Rain 2-3" per hour | 2022-08-23 | 06:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Lateral blockage and roots moved into main line after sudden hard rain. | Homeowner called to report basement | 200 Gallons | Basement area affected. | No | N/A | 2022-08-23 | 07:30 PM | 200 Gallons | 200 |  | Jetted main line from manhole at intersection of Clifton St. and Johnson Ave. toward 27 Swan Ave, La | Seymour | 27 Swan Ave, Seymour, CT
SEYMOUR WPCF, TOWN OF | Closed | Sewage Bypass | Dry | 2022-06-10 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Sewer main is cracked | Passerby | 1-2 Gallons per min .approx. 3240 gals per day | Visual seepage on pavement and amount of time leaking | Yes | Hoadley Pond Brook/Little River | 2022-06-15 | 08:00 PM | 15,800 gals. | 15800 |  | On 6/16/22 8:00am before construction repair began there was no seepage coming out of ground. Area h | Seymour | 14-16 Old Dr, Seymour, CT
16330

## SHELTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
SHELTON | Closed | Sewage Bypass | Dry | 2022-11-15 | 09:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | Cracked pipe filled with dirt. | City notified by a CBYD employee. | Less than 25 gallons | Visual | No |  | 2022-11-16 | 11:15 AM | Less than 25 gallons | 20 |  | Water was shut off 11/15/22. A new section of sewer lateral was installed 11/16/22. | Shelton | 92 Wooster St, Shelton, CT
SHELTON | Closed | Sewage Bypass | Dry | 2022-10-11 | 09:45 AM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | Small forced main plumbing disconnected in the manhole; a very small amount of sewer water was obser | Resident at 11 Birdseye Road Ext called DPW, DPW personnel went to ascertain disposition and therefo | Less than 50 gallons; When the City first arrived there was only tell tale signs of dampness on the | best guess after the fact. | No |  | 2022-10-11 | 10:30AM | 150 gallons of water in the manhole above the ejector pump chamber and possibly 25 gallons trickled | 25 |  | the vertical 2 1/2" PVC pipe coming out of the ejector pump was hooked back into the 2 1/2" PVC hori | Shelton | 11 Birdseye Rd Ext, Shelton, CT
45

## SIMSBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2022-06-29 | 11:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Roots | roots and Debris in private sewer line caused blockage and overflowed manhole | Contractors on site reported | 100 gallons | Notification time until overflow stopped | No |  | 2022-06-29 | 02:00 AM | 100 gallons | 100 |  | Private sewer system owned by Dyno Nobel | Simsbury | 640 Hopmeadow St, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2022-06-29 | 11:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Roots | Roots and debris in line caused blockage | Contractors on site reported overflowing manhole to Town | 100 Gallons | Time of reported overflow to time overflow stopped | No |  | 2022-06-29 | 12:15 PM | 100 Gallons | 100 |  | Jetted line to clear blockage, cleaned and disinfected area where overflow occurred | Simsbury | 660 Hopmeadow St, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2022-05-09 | 07:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | No cause given | Called into police | Estimate given as unknown | Estimate given as unknown | Yes | Stebbins Brook to Farmington River | 2022-05-09 | 08:30 AM | No estimate given |  |  | Line was jetted with flusher clearing the blockage. Manhole was rechecked once done. Area was spra | Simsbury | 536 Hopmeadow St, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2022-05-20 | 07:15 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Roots | The roots caught rags blocking the flow. | We were called by Dyno Nobel personnel Mike Powers. | 200 Gallons | A guess looking at the amount of water in our storage tank on the Town of Simsbury's Vacuum/Jetter | No |  | 2022-05-20 | 09:00 AM | 200 gallons | 200 |  | The line was jetted dislodging the clog and allow the flow to resume down the private lateral to the | Simsbury | 660 Hopmeadow St, Simsbury, CT
400

## SOUTH WINDSOR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2022-06-30 | 05:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Resident notified Public Works Department who called in Pollution Control personnel. | About 5000 gallons | By taking average daily flow and doing the math for 2.5 hours. | Yes | It went into the downstream storm drain on Avery Street, I am not sure where that drainage goes to. | 2022-06-30 | 07:30 PM | Approximately 5000 gallons | 5000 |  | Rag mass was removed from manhole | South Windsor | 839 Avery St, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2022-06-30 | 10:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | In addition to rags there were also large rocks. | Police discovered and called | About 5700 gallons | By using the wet well capacity and draw down rate of the upstream pump station | Yes | Avery Brook | 2022-07-01 | 04:00 AM | About 5700 gallons | 5700 |  | Blockages were cleared | South Windsor | 796 Avery St, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2022-07-11 | 10:00 AM | Treatment Plant | Partially Treated Raw Sewage | Other | When the gate to secondary clarifier 4 was reopened after maintenance water from the UV Chamber rush | An alarm came in on the SCADA system | About 4900 gallons of treated but non disinfected wastewater. | Based on flow and the time the UV was off. | Yes | Connecticut River | 2022-07-11 | 00:00 AM | About 4900 gallons | 4900 |  | Water level naturally came back up and UV turned back on | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-09-22 | 10:30AM | Treatment Plant | Partially Treated Raw Sewage | Other | Power loss | As soon as we lost power we knew there was a power disruption to UV | 3.05 MGD for about 10 minues | By using flow rate and time | Yes | Connecticut River | 2022-09-22 | 10:45 AM | About 22000 gallons | 22000 |  | Power came back, bulbs ramped up | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2022-08-18 | 03:45 PM | Treatment Plant | Raw Sewage | Electrical Equipment Failure | uv disinfection times out after a power interuptiondelay when uv is back up is built into program fo | scada alerted operator on call of loss of power at main sewage treatment plant | 25,625 gallons of plant effluent not disinfected | flow at time of incident times the duration of event | Yes | connecticut river | 2022-08-18 | 04:00 PM | 253625 | 253625 |  | Power came back | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2022-05-12 | 01:30 PM | Treatment Plant | Partially Treated Raw Sewage | Other | We needed to switch to generator power to do electrical maintenance which cause a brief lapse of UV. | We created the incident in order to do critical electrical inspection. | 21319 gallons of treated wastewater that was not properly disinfected. | By looking at flow rate and doing the math to determine what 10 minutes at 3.07 mgd is in actual gal | Yes | Connecticut River | 2022-05-12 | 01:45 PM | About 21319 gallons | 21319 |  | Generator power kicked on and brought bulbs back to full strength | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2022-08-16 | 03:30 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | A tree fell into wires near the treatment plant. In order to fix the issue power needed to be cut w | We transferred power so Eversource could make their repair. | Average of 2.7 MGD for 14 minutes before UV came back up to full strength, or about 26000 gallons | See above | Yes | Connecticut River | 2022-08-16 | 03:00 PM | 26000 gallons | 26000 |  | The UV system came back up to full strength | South Windsor | 1 Vibert Rd, South Windsor, CT
338544

## SOUTHINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2022-11-13 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Southington WPC staff received call about possible sewer line blockage. | 75 gallons | Estimate | No |  | 2022-11-13 | 04:30 PM | 75 gallons | 75 |  | Town of Southington WPC staff used Jet/Vac truck to relieve the blockage. | Southington | 17 Norton St, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2022-08-02 | 02:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Southington WPC staff were notified by restaurant owner that the restaurant's outdoor grease trap wa | 15 gallons | Estimate | No |  | 2022-08-02 | 04:30 PM | 15 gallons | 15 |  | Southington WPC staff jetted the sewer main to relieve the blockage. | Southington | 59 W Center St, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Snowmelt | 2022-03-01 | 08:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots |  | Engineering Department reached out to plant staff regarding water coming out of a manhole. | 50-500 gallons | Estimate | No |  | 2022-03-01 | 10:00 AM | 51-500 gallons | 450 |  | WPC Staff removed roots from manhole to allow wastewater to flow through the main. | Southington | 72 Norton St, Southington, CT
540

## STAFFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
STAFFORD | Closed | Sewage Bypass | Other | 2022-03-08 | 04:00 AM | Treatment Plant | Sludge Spill | Electrical Equipment Failure |  | At the start of the next morning, the shit Operator found RAS pumps off. | approx. 3 hours at 75 GPM | base flow coming into the plant at the time. | Yes | Willimantic River | 2022-03-08 | 07:15 AM | 13,500 gal |  | RAS pumps were turned on, Polymer was added to the RAS, Effluent filters were backwashed, | Stafford | 50 River Rd, Stafford, CT
13500

## STAMFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
STAMFORD | Closed | Sewage Bypass | Dry | 2022-09-12 | 11:45 AM' | Manhole | Raw Sewage | Electrical Equipment Failure | Mechanics arrived at Hobson Pump Station @11:15 a.m. today to complete routine inspection activities | A member from the general public notified WPCA of a sanitary sewer overflow. | 5 gallons | Wetted area was estimated. | No |  | 2022-09-12 | 12:00 PM | 5 gallons | 5 |  | WPCA electrician is working on determining where this power disconnect originated in the pump statio | Stamford | 69 Sea Beach Dr, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-10-09 | 09:00 PM | Treatment Plant | Sludge Spill | Sewage Line Blockage - Other | A blockage in Hydro Cyclone#1 caused sludge to spill into a roof drain and ultimately into a catch b | Discovered making my evening walk through of the plant. | less than 50 gal | Plant operator was in the building 1 hour prior and condition did not exist. judging by sludge on | No |  | 2022-10-09 | 09:00 PM | less than 50 gal | 45 |  | Pump turned off. | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-03-16 | 08:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | FOG (fats, oil, and grease) materials associated with both residential and commercial operations wer | Another City department reported the incident to WPCA. | 10 gals. | Wetted area was estimated. | No |  | 2022-03-16 | 08:15 AM | 10 gals. | 10 |  | Flow conditions were inspected and determined to be normal. | Stamford | 228 Stillwater Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-05-13 | 12:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Lateral to building compromised by sign construction on or near sidewalk. | Home owner noticed water coming from the base of newly installed street sign. Home owner stopped us | 20 gallons | Estimated by home owner. | Yes | Small amount of raw sewage reached the storm drain leading to L.I.S. | 2022-05-13 | 01:45 PM | 20 gallons | 20 |  | Line cleaned. | Stamford | 37 Southfield Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-01-06 | 07:15 AM | Manhole | Raw Sewage | Unknown | Crews responded to a sewer call and jetted line to alleviate blockage, i.e., grease, rags, etc. | Observations reported via Highways Department. | 1-5 gallons | Wetted area was estimated | No |  | 2022-01-06 | 10:00 AM | 1-5 gallons | 5 |  | Crews responded to a sewer call and jetted line to alleviate blockage, i.e., grease, rags, etc. | Stamford | 13 Seaton Rd, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-03-02 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | As WPCA jetted sewer line, FOG materials associated with nearby condominium complexes was observed a | Another City department reported the observation to WPCA. | Estimated quantity of wastewater bypassed from the conveyance system is approximately 150 gals. | Affected wetted area was estimated. | No |  | 2022-03-02 | 10:00 AM | Approximately 150 gals. | 150 |  | WPCA crew jetted surcharged line and disinfected affected surface areas. | Stamford | 263 Strawberry Hill Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-09-08 | 10:30AM | Sewer Main | Raw Sewage | Other | WPCA suspects a portion of the gravity sewer line is broken. | Service call was investigated. | Estimated discharge rate of 0.1 gpm. | Discharge rate was observed and estimated. | No |  | 2022-09-08 | 08:30 PM | 60 gallons | 60 |  | WPCA's contractor removed tree roots that cracked the sewer line and replaced with SDR-35 pipe and a | Stamford | 70 Halliwell Dr, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-12-19 | 07:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Collection main was allowing wastewater to flow, but may have had a partial blockage. Vactor recover | Reported by tenant. | Estimated as 1 gallon per minute for four hours. Approximately 240 gallons. | visual estimate | Yes | Storm drain system to LIS | 2022-12-19 | 11:45 PM' | Approximately 240 gallons. | 240 |  | Collection sewer mains cleaned by jetting and vac by SWPCA staff.Owner/Tenant contracted local drain | Stamford | 280 E Main St, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2022-05-09 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Both elevated levels of grease and rag materials were observed contributing to the blockage. | Another City department reported the observation to WPCA. | 3-6 gallons. | Wetted area was estimated. | No |  | 2022-05-09 | 09:30 AM | 3-6 gallons. | 6 |  | Affected areas were vacuumed and disinfected. | Stamford | 127 1st St, Stamford, CT
541

## STRATFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
STRATFORD | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-07 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Snow melt and rain combined increased flows causing solids carryover. | Operator on duty discovered dosage drop in UV. Took preventative measures including chemical additio | 1.125 MG | SCADA trending | Yes | Housatonic River | 2022-02-08 | 02:15 AM | 1.125 MG | 1125000 |  | See above comments. Corrective actions | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Dry | 2022-08-23 | 01:45 PM | Treatment Plant | Partially Treated Raw Sewage | Other | A software update was needed for the PLC. The communication with the PLC was lost during the upload. | Alarm | 67,000 gallons | SCADA flow trend | Yes | Housatonic River | 2022-08-23 | 02:00 PM | 67,000 gallons | 67000 |  | Upload was completed and the system returned to normal | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Dry | 2022-01-09 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Unknown | Secondary blankets were high. | UV alarm | 425,000 gallons | SCADA trend | Yes | Housatonic River | 2022-01-09 | 11:45 PM' | 425,000 Gallons | 425000 |  | Chemical addition to aid settling. Mixers and blowers shut off or turned down. RAS control | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Dry | 2022-07-30 | 04:30 AM | Treatment Plant | Partially Treated Raw Sewage | Select... | Electrical failure | Alarms | 250,000 gallons | SCADA flow | Yes | Housatonic river | 2022-07-30 | 00:00 AM | 250,000 gallons | 250000 |  | Replaced part | Stratford | 105 Beacon Point Rd, Stratford, CT
1867000

## SUFFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
SUFFIELD | Closed | Sewage Bypass | Dry | 2022-02-16 | 09:30 PM | Sewer Main | Raw Sewage | Other | Force main break | Home Owner from #45 Conservation Drive | 420 gallons | Used Mission data on gallons for each pump | No |  | 2022-02-16 | 10:15 AM | 420 gallons |  | 2.5" force main pipe was dug up. Old coupling was broke in half. 24" pipe section of schedule 80 p | Suffield | 45 Conservation Rd, Suffield, CT
420

## TRUMBULL
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
TRUMBULL | Closed | Sewage Bypass | Dry | 2022-07-26 | 03:00 PM | Sewer Main | Raw Sewage | Other | Break in force main pipe | Bridgeport WPCA notice water coming from pavement | hard estimate rate of discharge pavement wet with sewege | just debris on ground no water witnessed at this timeGrass has grey coating along road way | Yes | pequonnock river | 2022-07-27 | 03:30 AM | 498,000 gal | 498000 |  | The defective 10' section of pipe was replaced with a new 20" dia. DI pipe | Bridgeport | 3296 E Main St, Bridgeport, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2022-09-01 | 12:30 PM | Manhole | Raw Sewage | Other | Kovaks construction digging to locate break of force main. Due to the depth of the forced main Burns | Bridgeport line cleaning crew | Unknown water was going into storm line size of garden hose | unknown | Yes | storm line ends up in Bridgeport lake forest | 2022-09-01 | 01:30 PM | unknown | 5000 |  | The defective section of was removed | Bridgeport | 1741 Old Town Rd, Bridgeport, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2022-05-03 | 12:30 PM | Sewer Main | Raw Sewage | Other | Small hole in 10" Force Main | Resident called in noticed the side walk was wet and had thought is was a water main break. | Small amount of Discharge in grassy area | best guess there was minimal discharge do to both 10" and 8" force main running from same station | No |  | 2022-05-31 | 07:30 PM | best guess estimate would be under 100 gal | 95 |  | was able to shut down 10" line immediately dug line found quarter size whole in pipe was able to put | Trumbull | 6466 Main St, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2022-08-26 | 03:00 PM | Sewer Main | Raw Sewage | Other | Pipes strapped to side of covert fell and broke | Resident at 52 Kroger called in complained about smell | Unknown | not able to determine | Yes | Island Brook underneath Merritt parkway | 2022-08-26 | 09:30 PM | It is unknown when the brackets retaining two sections of pipe failed allowing them to dislocated fr | 10000 |  | The missing pipe was replaced with 8" DI pipe and new brackets were install on each section of p | Trumbull | 52 Koger Rd, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2022-03-31 | 01:00 PM | Pump Station | Raw Sewage | Other | Burns Construction Company installing water main hit force main at our Reservoir pump Station | Contractor notified us as soon as they hit it. | Trash pump rated at 88 GPM pumping from hole where break isline repaired 2:41 PMEstimated Quantity | Trash pump rated for 88 GPM | Yes | Storm water stream | 2022-03-31 | 02:45 PM | Pumping lasted about 1hr and 1/2pump is rated for 88 gpm final estimate 8,000.00 gals | 8000 |  | we have a portable by-pass pump installed at station while pipe was being replacedhole was containin | Trumbull | 2595 Reservoir Ave, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2022-04-08 | 02:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Line Collapse | DPW Crew | 150 gpm for 1 hour estimated 9000.00 gals | Reference sheet for estimating sewer flow rate from overflowing sewer manholes150 GPM | No |  | 2022-04-09 | 02:45 PM | 9000.00 Gals | 9000 |  | Whitney Station shut down McVac service 5 trucks for pumping station to by pass line repaired by Bur | Trumbull | Main St, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2022-11-10 | 10:00 AM | Sewer Main | Raw Sewage | Other | Force main failure - Lateral crack approximately | Workman on site | 130 Gal/min | approximated by visual observation | Yes | Pequonnock River | 2022-11-10 | 08:30 PM | 290,000 gal | 290000 |  | The deflective 12 foot section of pipe was replaced. We are in the process of replacing 1000 feet o | Bridgeport | 1875 Noble Ave, Bridgeport, CT
820095

## MANSFIELD - UCONN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
UNIVERSITY OF CONNECTICUT | Closed | Sewage Bypass | Dry | 2022-09-16 | 10:00 AM | Sewer Main | Raw Sewage | Unknown | Likely due to age of pipe | Notified and discovered by Facilities Operations personnel. | minimal, < 100 gal | estimate | No | N/A | 2022-09-16 | 01:45 AM | approximately 100 gallons | 100 |  | A contractor responded, repaired/replaced the section of sewer main. | Mansfield | Ledoyt Rd, Mansfield, CT
UNIVERSITY OF CONNECTICUT | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-04-06 | 02:30 PM | Sewer Main | Raw Sewage | Other | Main break due to age of/condition of pipe | Public Works was notified and contacted WPCF. | 5,000 - 10,000 gallons | Estimate | No | went to the ground/field adjacent to the horse paddock. | 2022-04-06 | 07:30 AM | 5,000-10,000 gallons | 9000 |  | Contractor (Suburban) assisted with pumping at the nearby lift station and Public Works/Contractor | Mansfield | 1689 Horsebarn Hill Rd, Mansfield, CT
9100

## GROTON _ USN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-03-21 | 11:45 AM' | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | The incident was reported to the PWD staff. | Site personnel estimated that less than 20 gallons of liquid (no solids) were released. | The quantity was estimated by PWD personnel responding to the incident. | No |  | 2022-03-21 | 12:00 PM | Site personnel estimated that less than 20 gallons of liquid (no solids) were released. | 20 |  | PWD staff flushed the lines to clear the grease blockage and applied lime at the manhole to neutrali | Groton | 140 Dewey Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-10-10 | 02:15 AM | Pump Station | Raw Sewage | Other | Line broke while pumping. Reason why line broke unknown. | USS Colorado was pumping on Pier 31 and while pumping, they saw the line broke. The pump was immedia | 10 Gallons | Visual | Yes | Thames River | 2022-10-10 | 02:30 AM | 10 Gallons | 10 |  | By the time Subase Fire Department arrived on scene, there was nothing they could do. The sewage alr | Groton | 1 Crystal Lake Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-02-03 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | It is not known what is blocking the sewage line. | Boat personnel were flushing water (not sewage) into the sanitary line through a hose and the hose r | Unknown. It is possible that a small amount of sewage was released into the Thames River; however, t | Quantity estimated by Public Works personnel who responded to the incident. | Yes | Thames River | 2022-02-03 | 10:00 AM | Unknown. It is possible that a small amount of sewage was released into the Thames River; however, t | 5 |  | The Public Works Department took the riser out of service until it can be repaired. A tanker was bro | Groton | Amberjack Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed |  | Dry | 2022-09-19 | 04:45 PM | Pump Station | Raw Sewage | Other | Sewage line broken. | Personnel on site conducting work noticed it immediately and shut it off. | Less than a half gallon | Visual | Yes | Thames River | 2022-09-19 | 05:15 AM | Roughly a cup. | 1 |  | Made sure the leak was secured and public works is called to fix the leaky pipe. They are diverting | Groton | 1 Crystal Lake Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-02-27 | 06:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other |  | Sewage seen coming up past manhole in street in residential area, trouble call placed to Navy Public | Less than 100 gallons | Visual observation by Navy representatives responding to bypass event. | No |  | 2022-02-27 | 10:30 PM | Less than 100 gallons. | 95 |  | High-pressure water jet used to clear blockage in sewer pipe under the road. | Groton | 126 Driftwood Cir, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-01-02 | 05:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Reported by tenant to Fire Dept. | Report from our regional dispatch center gives a low rate of discharge. UEM estimate is ~100 gallon | Called in by on-scene response (Fire Dept). | No | N/A | 2022-01-02 | 07:30 PM | ~100 gallons liquid | 95 |  | Jetted the line, observed no further backups between now and then. PWD recently sent out a reminder | Groton | 148 Michigan Dr, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-05-31 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Reported by occupants of community center after backup seen at floor drain in facility basement. | Less than 5 gallons. | Visual observation. | No | N/A | 2022-05-31 | 11:30 AM | Less than 5 gallons. | 4 |  | Navy PW personnel cleared interior pipe blockage, Beacon Point Homes personnel (housing area and com | Groton | 45 Proteus Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-05-20 | 10:00 AM | Manhole | Raw Sewage | Unknown | Split PVC pipe section | Reported by Nautilus Museum and Utilities to Fire Department, Regional Dispatch Center notified Envi | 50 gallons over a 4 x 50ft area, small amount into Stormdrain. | FD and Utilities personnel estimate off flow. | No | N/A Outfall pipe is approx 4 Ft diameter. | 2022-05-24 | 02:00 PM | <100 gallons | 95 |  | Cleared brush, excavated and installed shoring, hand dug to cutout, replaced 18" piece of 4" PVC pip | Groton | Crystal Lake Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-05-24 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Bypass seen by Navy PW utility personnel when driving in that area of Navy base. | Estimated as 30 gallons, no solids seen. | Visual observation | No |  | 2022-05-24 | 11:30 AM | 30 gallons of sewage water, no solids present | 30 |  | Navy PW utility personnel used water jet equipment to remove blockage in sanitary pipeline, stop byp | Groton | 410 Tang Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-12-01 | 08:45 PM | Sewer Main | Raw Sewage | Unknown | Sewer blockage. | Resident reporting. | Unknown. | N/A | No |  | 2022-12-02 | 02:30 PM | Unknown | 5 |  | Blockage cleared by SUBASE PWD utilities. | Groton | 54 Magnolia Dr, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2022-05-24 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Navy PW utility personnel noted sewage backup in lot themselves while driving in that location on Na | Estimated as 30 gallons of water (no solids visible) | Visual observation. | No |  | 2022-05-24 | 11:30 AM | Same, no change, 30 gallons | 30 |  | Navy PW utilities used water jet equipment to remove blockage (believed to be grease buildup). Lot l | Groton | 410 Tang Ave, Groton, CT
390

## VERNON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
VERNON WPCF | Closed | Sewage Bypass | Dry | 2022-01-18 | 09:00 PM | Treatment Plant | Sludge Spill | Other | East Secondary Scum Well Overflowed onto the Ground. Pump to Keep Wet Well from Overflowing was not | Security Guard Noticed Overflowing Well on Rounds | 50 Gallons EST | Visual Estimate. No Trending on SCADA to Determine when overflow level reached. | No |  | 2022-01-18 | 09:15 PM | 50 Gallons EST | 50 |  | Pump Put Back in Auto and Lime was Applied to Affected Area. Operator and Security Guard to Monitor | Vernon | 100 Windsorville Rd, Vernon, CT
VERNON WPCF | Closed | Sewage Bypass | Dry | 2022-01-24 | 09:00 AM | Pump Station | Raw Sewage | Other | Force Main Break | Sewage Surfacing on Ground | 1,000 gallons per hour | Visual Estimate | Yes | Hockanum River | 2022-01-24 | 04:45 PM | 10,000 gallons | 10000 |  | Pump station was shutdown and Inlet Flow manholes were pumped out by septic trucks all day to preven | Vernon | 25 Hartford Turnpike, Vernon, CT
VERNON WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-05-28 | 05:00 PM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure | Temporary bypass pumps did not handle plant flows and auto dialer did not work for DEEP approved byp | Security guard noticed secondaries overflowing onto ground and called on call WPCF supervisor. | 127,106 gallons. | Influent flow meter readings for duration of bypass. | Yes | Hockanum River | 2022-05-28 | 05:45 AM | 127,106 gallons. | 127106 |  | Reduced RAS flow and Influent flow to stop overflow. Pump vendor is in route to troubleshoot alarm a | Vernon | 100 Windsorville Rd, Vernon, CT
VERNON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-06-27 | 03:15 PM | Treatment Plant | Partially Treated Raw Sewage | Other | Breakdown of Bypass created a syphon effect from Aeration Tank 5 that flowed to catch basin | Syphon effect was immediately recognized and the upper connection was broken within a ten minute per | <500 gallons | Pipe size and time of leak | Yes | Hockanum River | 2022-06-27 | 03:30 PM | <500 gallons | 450 |  | pipe connection on top of tank was opened | Vernon | 100 Windsorville Rd, Vernon, CT
VERNON WPCF | Closed | Sewage Bypass | Dry | 2022-12-15 | 12:15 PM | Treatment Plant | Partially Treated Raw Sewage | Other | Vendor working on new bypass gate and it unexplainably closed which sent wastewater to inactive wet | Wastewater coming out of wet well. | 5,000 est | influent flow meter | Yes | Hockanum River | 2022-12-15 | 12:15 PM | 5,000 gallons est | 5000 |  | Out of service wet well was put in service while gate issue was corrected. | Vernon | 100 Windsorville Rd, Vernon, CT
142606

## WATERBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-06-29 | 11:00 AM | Basement | Raw Sewage | Other | CCTV camerawork showed roots and rocks were the cause of the blockage | Resident called customer service | 50-100 | Visually | No |  | 2022-06-29 | 11:30 AM | 75 gallons | 75 |  | A jetter truck dispatched to clear blockage and CCTV to determine cause. | Waterbury | 17 Blake St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-08-04 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Unknown at this time It was determined through camera work that roots were the cause of the blockage | Q- alert complaint | 1-50 gallons | visual | No | N/A | 2022-08-04 | 11:00 AM | 70 gallons | 70 |  | Jetter truck dispatched to release blockage. Roots where found to be the cause. | Waterbury | 209 Academy Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-01-09 | 06:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Roots and grease accumulated and created a blockage in the ROW | Homeowner called collections supervisor | 160 gallons | Visual and dimensions of the bypass area (16ft x 16 ft x 0.8 ft) | No | N/A | 2022-01-09 | 07:00 PM | 160 gallons | 160 |  | Crew found the manholes running surcharged so approximately 400 feet of the collections system (ROW | Waterbury | 215 Stoddard Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-04-29 | 11:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Rags where found to be the cause of the ByPass. | Water Dept. noticed the ByPass while doing a routine complaint. | 25 gallons per minute | SSO volume calculator | No |  | 2022-04-30 | 00:30 AM | 225 gallons | 225 |  | A jetter truck was dispatched to jet the line to release the blockage. | Waterbury | 975 Meriden Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-02-20 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Water Department reported bypass | 300-400 gallons | SSO volume calculation chart | Yes | Mad River | 2022-02-20 | 11:00 AM | 400 gallons | 400 |  | Line was jetted to clear the blockage | Waterbury | Rawley Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-08-29 | 03:30 PM | Manhole | Raw Sewage | Other | Sticks and rags | DPH called Collections Manager | 150 gallons | overflow calculator | Yes | Steele Brook interceptor | 2022-08-29 | 04:15 PM | 150 gallons | 150 |  | Jetted line to remove blockage, changed all upstream manhole from a single hole cover to no hole cov | Waterbury | 229 Whitewood Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-11-17 | 12:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease was found to be the main cause of the blockage | Phone call by Street Department | 2,000 gallons | Overflow manhole estimator diagram | No |  | 2022-11-17 | 12:45 PM | 2,000 gallons | 2000 |  | Jetted line to release the blockage. The area was cleaned with water and the use of a vac truck to c | Waterbury | Hamilton Park Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-01-08 | 05:15 PM | Pump Station | Raw Sewage | Sewage Line Blockage - Other | It is believed a blockage in the system created a surcharge into the wet well | SCADA alarm | 50 gallons approx. (bypass was not witnessed) | Visual - Since bypass was not witnessed, the collections operator visually estimated volume by obser | No | N/A | 2022-01-08 | 06:30 PM | 50 gallons approx. (bypass was not witnessed) | 50 |  | Crew cycled pumps, inspected and cleaned the floats and monitored the station for several cycles | Waterbury | 52 Terrell Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2022-04-07 | 08:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | approximately 2 inches of rain in (5 hours). One of 8 clarifiers was out-of-service for construction | Operator discovered filtering building was overflowing when doing rounds during the storm event. SCA | 0.8 MG | Calculate the excess of partially treated effluent that went over the 4 weirs (4 filters) in the fil | Yes | Naugatuck River | 2022-04-08 | 02:00 AM | 0.8 MG | 800000 |  | operators tried to maximize the capacity of the plant so permitted outfall 002 was not activated. Ra | Waterbury | 210 Municipal Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-06-10 | 03:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | unknown at this time On 6-13-22 CCTV work was done to assess the pipe condition. No defects were fo | Phone call by the Waterbury Fire D | 50-100 gallons | Visual | No |  | 2022-06-10 | 04:30 PM | 100 Gallons | 100 |  | Jetter truck was dispatched to release blockage. | Waterbury | 9 Easton Ave, Waterbury, CT
803230
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-06-21 | 10:15 AM | Lateral - Private | Raw Sewage | Unknown | This is a Private Lateral curb box blockage | A Refuge Department noticed the curb box releasing and submitted a Qalert. | 1-50 gallons | Visual from Jacobs field crew | No |  | 2022-06-25 | 11:15 AM | DPH report of 50 gallons final quanity | 50 |  | Homeowner hired a plumber to clear blockage | Waterbury | 60 Englewood Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-12-21 | 12:30 PM | Lateral - Private | Raw Sewage | Other | unknown | Qalert complaint | 75-125 gallons | visual | No |  | 2022-12-22 | 03:00 PM | DPH estimated 50 gallons | 50 |  | Owner cleared blockage and cleaned area with bleach and water | Waterbury | 85 Ridgewood St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-07-07 | 10:45 AM | Lateral - Private | Raw Sewage | Unknown | Private bypass | Resident at 81 Walnut st called to report water in the driveway. Bypass was actually coming from 97 | 50-100 gallons | Visually | Yes | Mad River | 2022-07-12 | 02:00 PM | DPH reports 100 gallons | 100 |  | DPH is overseeing the repair and cleanup | Waterbury | 97 Walnut St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-10-26 | 04:30 PM | Lateral - Private | Raw Sewage | Unknown | Blockage in the private lateral of 304 Willow St. | DPH Qalert. Number 133198 | 20-50 gallons | visual | No |  | 2022-10-28 | 03:00 PM | DPH reports final discharge at 75 gallons | 75 |  | contractor hired to clear blockage | Waterbury | 304 Willow St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-12-22 | 11:45 AM' | Lateral - Private | Raw Sewage | Other | blockage. Unknown | DPH had a call from a concerned citizen. | 20-30 gallons | visual | No |  | 2022-12-23 | 10:00 AM | DPH reports 75 gallons | 75 |  | owner hired A1 plumbing to clear the blockage and sanitize with bleach and water on 12-22-22 | Waterbury | 19 Taylor St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-02-13 | 02:15 PM | Lateral - Private | Raw Sewage | Other | Blockage in private lateral | Resident sent a request online | 100 gallons | Visual | No | N/A | 2022-02-15 | 11:15 AM | 100 gallons | 100 |  | DPH contacted the landlord and had him perform the necessary repairs to clear the blockage | Waterbury | 242 Rawley Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-03-01 | 09:45 AM | Lateral - Private | Raw Sewage | Unknown |  | Qalert from the call center. | 1-50 gallons | Visual | No | N/A | 2022-03-04 | 08:00 AM | 50 gallons | 50 |  | DPH was to call Prospect Sanitation to clear blockage. DPH will confirm final quantity and date. | Waterbury | 16 Pine St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-11-22 | 10:15 AM | Lateral - Private | Raw Sewage | Unknown | Private curb box blockage. | Qalert system | 10-30 gallons | Visual | No |  | 2022-11-25 | 12:00 PM | Final quantity determined by DPH is 70 gallons | 70 |  | Landlord hired a contractor to clear the blockage and cleanup the area with bleach and water. | Waterbury | 86 Wood St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-04-28 | 10:15 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Not known. This is a private Lateral | WPC employee drove by and called WPCF | 100 gallons | estimated by DPH | No |  | 2022-04-29 | 09:30 AM | 100 gallons | 100 |  | Homeowner hired a contractor to clear blockage | Waterbury | 208 Boyden St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-10-04 | 09:15 AM | Lateral - Private | Raw Sewage | Unknown | Unknown at this time. DPH has been notified to monitor | DPH received a Qalert | 10-30 gallons | Visual | No |  | 2022-10-07 | 03:00 PM | 50 gallons | 50 |  | DPH hired contractor to clear blockage | Waterbury | 123 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-11-28 | 11:30 AM | Lateral - Private | Raw Sewage | Unknown | Blockage in a private curb box | Qalert complaint | 10-30 gallons | Visual | No | n/a | 2022-11-29 | 03:00 PM | 50 gallons | 50 |  | DPH contacted Landlord to clear blockage. | Waterbury | 275 Bishop St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-05-20 | 10:15 AM | Lateral - Private | Raw Sewage | Unknown | Unknown. This is a Private bypass. | Neibor called the DPH who then called WPCF | 1-50 gallons | visual | No |  | 2022-05-24 | 02:45 PM | Waiting on DPH report of Quantity | 50 |  | DPH is monitoring the repair | Waterbury | 111 Draher St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-01-13 | 09:45 AM | Lateral - Private | Raw Sewage | Unknown | Unknown at this time. Bypass was referred to DPH | Resident called customer service | Unknown | Unknown | No | N/A | 2022-01-13 | 10:30AM | Unknown - bypass was referred to DPH | 50 |  | Bypass was referred to DPH | Waterbury | 238 Bunker Hill Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-05-04 | 10:30AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown. This is a private lateral issue. DPH has been notified to oversee the repair. | Called in by Homeowner | 1-50 gallons | visual | No | N/A | 2022-05-05 | 03:00 PM | 100 gallons estimated by DPH | 100 |  | DPH and the homeowner worked together to resolve issue. | Waterbury | 40 Vermont St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-09-19 | 02:15 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | This is a private By-Pass and DPH has been notified to investigate and monitor. | Qalert complaint | 1-25 | Visual | No |  | 2022-09-20 | 09:30 AM | 15 gallons estimated by DPH | 15 |  | A contractor was called in to clear the blockage | Waterbury | 56 Ridgewood St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-02-08 | 10:15 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | According to DPH inspector private Sewer lateral had blockage of grease and rags | Ted called to report sewer discharge | Unknown | Unknown | Yes | Mad River | 2022-02-09 | 10:00 AM | 50 gallons | 50 |  | DPH Inspector contacted manager at CVS - 526 Meriden Road, who hired Prospect Sanitation to clear th | Waterbury | 526 Meriden Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-03-23 | 10:45 AM | Lateral - Private | Raw Sewage | Unknown |  | Resident at 56 Sidney St reported an odor complaint. When investigating, it was determined the priva | 1-500 gallons | Unknown | No | N/A | 2022-03-24 | 10:30AM | DPH has estimated the final volume to be 200 gallons | 200 |  | DPH hired a contractor to clear the blockage | Waterbury | 56 Sidney St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-01-12 | 01:30 PM | Lateral - Private | Raw Sewage | Other | Blockage in private sewer lateral | Sewer complaint by Anthony Riviere | 50 gallons | DPH determined total volume | No | N/A | 2022-01-12 | 04:00 PM | 50 gallons | 50 |  | DPH had homeowner hire a company that clear the blockage in private lateral. | Waterbury | 49 Cassidy Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-01-28 | 12:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Sewage flowing from private sanitary line into the intersection of Mark Lane and Industry Lane | City's Engineering staff | 100 gallons | DPH Inspector | No | N/A | 2022-01-28 | 06:45 PM | 100 gallons | 100 |  | Refer to DPH as per ERP, DPH Inspector contacted landlord, who hired American Rooter to clear the bl | Waterbury | 100 Mark Ln, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-02-11 | 11:00 AM | Lateral - Private | Raw Sewage | Other | Blockage in private lateral | Resident called customer service | 150 gallons | Estimated by DPH Inspector | No | N/A | 2022-02-14 | 03:30 PM | 150 gallons | 150 |  | DPH contacted landlord and had him perform the necessary repairs to clear the blockage | Waterbury | 10 Marley Pl, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-01-04 | 10:45 AM | Lateral - Private | Raw Sewage | Unknown | City's sewer line was running without any obstructions so it seemed like the private lateral or buil | Tenant called customer service | 0-50 gallons | Visual | No | N/A | 2022-01-10 | 10:45 AM | 50 gallons | 50 |  | When the crew arrived to location, bypass was ceased. The crew checked the sewer collection system a | Waterbury | 23 Bergin Cir, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-02-08 | 01:45 AM | Lateral - Private | Raw Sewage | Unknown |  | Resident called sewer discharge from curb box to Admin Utility Division | Unknown | Unknown | No |  | 2022-02-09 | 11:00 AM | 5 gallons | 5 |  | DPH Inspector contacted landlord regarding the sewage bypass. Landlord hired a contractor to clear | Waterbury | 26 Wildwood Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-03-08 | 08:45 AM | Lateral - Private | Raw Sewage | Unknown | This is a private lateral curb box. DPH is investigating | Waterbury Engineering contacted DPH and they called the Collections Department to investigate. | 1-50 gallons | Visual | No | N/A | 2022-03-11 | 11:45 AM' | 50 gallons | 50 |  | Private ByPass was sent to the Health Department to Monitor and ensure the problem gets resolved. | Waterbury | 47 Woodruff St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2022-10-24 | 12:15 PM | Lateral - Private | Raw Sewage | Unknown | Discharging on to the driveway from there cleanout. | This was a follow up visit by field staff | 1-50 gallons | visual | No |  | 2022-10-26 | 10:00 AM | DPH estimated 50 gallons | 50 |  | Landlord hired contractor to clear blockage and clear the area with clean water. | Waterbury | 103 Holly St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-12-20 | 02:15 PM | Lateral - Private | Raw Sewage | Unknown |  | Qalert system complaint | 10-20 gallons | visual on grass | No |  | 2022-12-26 | 10:00 AM | DPH reports 100 gallons | 100 |  | DPH reports that the owner cleared blockage on 12-24-22 and sanitized with bleach and water | Waterbury | 54 Woodlawn Terrace, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-08-07 | 10:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other |  | Phone message from landlord | 25-75 gallons | visual | No |  | 2022-08-09 | 09:00 AM | DPH reports 50 gallons | 50 |  | Landlord called in contractor to clear blockage in the lateral | Waterbury | 1764 E Main St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-08-15 | 12:45 PM | Lateral - Private | Raw Sewage | Unknown |  | WPCF responded to a sewer complaint from the address above. | 1-25 gallons | visual | No |  | 2022-08-19 | 11:45 AM' | Unknown as this time. | 25 |  | DPH is monitoring the progress and resolution of the issue. | Waterbury | 5 Harriet Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-12-19 | 10:30AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | This is a private lateral blockage. cause is unknown | Street Dept foreman | 50-100 gallons | Visual | No |  | 2022-12-22 | 10:00 AM | DPH reports 50 gallons | 50 |  | DPH reported the owner cleared the blockage and washed down the area and sanitized with bleach and w | Waterbury | 12 Marley Pl, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2022-03-14 | 01:45 PM | Select... | Raw Sewage | Unknown | Blockage in a private curb box .. | Resident called in by Qalert. | 1-50 gallons | Visual | No |  | 2022-03-18 | 10:30AM | 50 gallons | 50 |  | The private ByPass is being monitored by DPH at this time. | Waterbury | 57 River St, Waterbury, CT

## WEST HAVEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-04-11 | 07:30 AM | Treatment Plant | Raw Sewage | Electrical Equipment Failure | One of the two wet well pumps failed. It is being repaired today. | Ryan Festa was in the parking lot and noticed it. | 20-75 gallons. | estimation. | Yes | New Haven Harbor. | 2022-04-11 | 07:45 AM | 20-75 gallons. | 55 |  | Flow to the wet well was stopped and pump is being repaired. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-12-20 | 03:15 PM | Manhole | Raw Sewage | Electrical Equipment Failure | Rodents ate wires | Routine checks | 150 gallons | Visual inspection | Yes | Oyster river | 2022-12-20 | 04:15 PM | 150 gallons | 150 |  | Rewired damage electrical | West Haven | 160 Woodmont Rd, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-03-16 | 09:30 PM | Pump Station | Raw Sewage | Electrical Equipment Failure | pumps tripped | homeowner saw manhole seeping | 5 gallons | visual inspection | No |  | 2022-03-16 | 10:00 | 5 gals | 5 |  |  | West Haven | 44 Morrissey Ln, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2022-09-06 | 12:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Flooding | Visual | Approx 1000 gallons | Visual | Yes | Oyster river | 2022-09-06 | 05:45 PM | Appro. 1000 Gallons | 1000 |  | Rain event | West Haven | 171 Beatrice Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-09-06 | 07:00 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | Excessive flows caused the bypass. | The operators on staff noticed the bypass. | Over 20 million gallons for the day with solids escaping. | An estimation. | Yes | The New Haven Harbor. | 2022-09-07 | 01:00 AM | Over 20 million gallons for the day with a lot of solids lost. | 20000000 |  | The rain stopped and everything went back to normal. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2022-09-06 | 09:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Flooding in area | Visual and high well alarm | 500 to. 1000 gallons | Visual | Yes | West river | 2022-09-06 | 04:45 PM | Approx. 1000 gallons | 1000 |  | Tain event | West Haven | 165 Front Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-04-04 | 01:00 PM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | One wet well pump could not keep up with flow, resulting in an overflow into parking lot. | Ryan Festa noticed the pit overflow around 1 pm. | 25-50 gallons of wastewater. | A visual inspection. | Yes | New Haven harbor via storm drain. | 2022-04-04 | 01:30 PM | 25-50 gallons of wastewater. | 45 |  | Both pumps are back online and Ryan Festa is cleaning up the mess. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-05-23 | 07:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Mechanical Equipment Failure | Main RAS line has been taken offline. Bypass line set up, but solids are washing out | Plant personal | Hard to tell- going to estimate 200-800 gallons an hour. | Estimation | Yes | New Haven Habor | 2022-05-24 | 03:00 PM | Several thousand gallons | 3000 |  | RAS line will be repaired and hopefully done by Tuesday/Wednesday. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-05-19 | 09:00 PM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | Belt filter press wet well overflow due to pumps not keeping up in auto. | Operator Ryan Festa noticed overflow going into parking lot. | 10-25 gallons | Estimation by Ryan Festa | Yes | New Haven Harbor | 2022-05-19 | 09:30 PM | 10-25 gallons | 20 |  | Put pumps into hand, shut off press to let wet well empty. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-05-23 | 07:00 AM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | RAS line being repaired by contractors. Using a bypass line and some solids washing out. | Plant personal. | Hard to estimate 200-600 gallons per hour. | estimation | Yes | New Haven Habor | 2022-05-24 | 03:00 PM | It will end up being serval thousand gallons. | 3000 |  | RAS line will hopefully be repaired by Tues/Wed and West Haven will stop washing out. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-10-14 | 11:00 AM | Manhole | Raw Sewage | Mechanical Equipment Failure | Bar screen tripped overload. | Public works called in mh overflowing | 100 gallons | Visual | Yes | Old field creek | 2022-10-14 | 11:30 | 100 gallons | 100 |  |  | West Haven | 98 Blohm St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-12-04 | 05:00 PM | Treatment Plant | Raw Sewage | Other | The Grit spill in the parking lot was caused by the grit dumpster accidently tipping over. | Ryan Festa was trying to empty the grit dumpster and it tipped over. | About two gallons went down a parking lot storm drain. | Visual inspection. | Yes | New Haven Sound | 2022-12-04 | 06:00 PM | About 2 gallons reached the New Haven Sound. The rest of the Grit was shoveled up by Ryan Festa. | 2 |  | Ryan Festa shoveled up the mess, cleaning everything up. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-09-29 | 08:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | called in be resident | 5 to 10 gallons | visual insoection | No |  | 2022-09-29 | 08:45 AM | 5 to 10 gallons | 8 |  | jetted line to remove blockage | West Haven | 175 Canton St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-01-18 | 01:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  |  | approx 10 gallons | bypass was in the building of 901 boston post rd and came out of the buildings cleanouts. | No |  | 2022-01-18 | 02:00 PM | 10 gals | 10 |  | called service master to clean the buildings | West Haven | 901 Boston Post Rd, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-10-11 | 12:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Manholes in wooded easment blocked by grease roots and rags | Homeowner odor complaint | 100 gallons | Visual | No |  | 2022-10-11 | 01:15 PM | 100 gallons | 100 |  | Jetted line | West Haven | 51 Carlson Rd, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-11-09 | 08:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | easment has no vehicle access to maintain line properly need to build access rd to maintain mh in sw | west haven pd | 70 gallons | visual inspection | No |  | 2022-11-09 | 09:15 PM | 70 gallons | 70 |  | jetted blockage 1000 ft | West Haven | 300 Meloy Rd, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-03-15 | 00:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | homeowner saw manhole overflowing | 5 gallons | visual inspection | No |  | 2022-03-15 | 04:45 PM | 5 gallons | 5 |  | Jetted the plugged line and relieved it. | West Haven | 422 Jones Hill Rd, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-05-05 | 10:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | homeowner | approx 25 gallons | visual | No |  | 2022-05-05 | 11:15 PM | 25 gallons | 25 |  | jetted line 200 ft | West Haven | 74 Harold St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-01-21 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | phone call to dispatch | approx 20gals | size of wetted area | No |  | 2022-01-21 | 10:00 AM | approx 20gals | 20 |  | we jetted the line 400ftwill follow up with routine maintenance. | West Haven | 26 Cove Brook Rd, West Haven, CT
20008615
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-05-25 | 11:00 AM | Manhole | Raw Sewage | Unknown |  | called in to wpca but was a private line | 45 gallons | visual | No |  | 2022-05-25 | 01:30 PM | 45 gallons | 45 |  | apt complex called in plumber to jet line | West Haven | 5 Treat St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-06-12 | 07:45 AM | Lateral - Private | Raw Sewage | Mechanical Equipment Failure | ongoing problem with mcdonalds workers are dumping grease possible floor drains and pumping system h | fire dept due to accident caused by grease | approx 75 gallons hard to determine due to spreading by car traffic | visual | Yes | possible west river there is a catch basin in lot that drains to river west river is downstream of s | 2022-06-12 | 11:30 AM | approx 75 gallons | 75 |  | DEEP ON SCENE. septic truck pumped well. | West Haven | 1129 Campbell Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2022-05-23 | 04:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | managment comp. for rental property | 5000gallons | pump truck estimated gallons | No |  | 2022-05-23 | 05:30 AM | 5000 gallons | 0 |  | jetted blockage/ following up with additional jetting and cctv next day | West Haven | 8 Knox St, West Haven, CT

## WESTPORT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
WESTPORT | Closed | Sewage Bypass | Rain 1-2" per hour | 2022-07-19 | 00:45 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | hole in the bottom of pipe. | Call from stop and shop manager. | 500-1000 | Estimated | No |  | 2022-07-19 | 04:30 PM | 1000 |  | The Repair was fixed with a clamp. | Westport | 1790 Post Rd E, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2022-05-19 | 04:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other |  | Some one called in from stop & Shop and the Fire Department | 501 - 1000 gallons | Estimated | No |  | 2022-05-20 | 05:30 AM | 1000 |  | The repair was resolved with a clamp | Westport | 1780 Post Rd E, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2022-08-15 | 10:15 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | broken sewer main | someone from stop & shop called it in. | 500-1000 gals | estimate | No |  | 2022-08-15 | 08:00 PM | 500 |  | Replace 6 foot Piece of 10" pipe. | Westport | 1790 Post Rd E, Westport, CT
2500

## WINDHAM-WILLIMANTIC
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | DEEP Estimation | How was Final Volume Determined | How incident was resolved | Municipality | Address
WINDHAM TOWN OF (Willimantic) | Closed | Sewage Bypass | Dry | 2022-01-20 | 03:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Blockage caused by greasy rag buildup in line in front or residence. | Homeowner working in basement. | <50 gals. | Area of floor effected. | No |  | 2022-01-20 | 04:00 PM | <50 gallons | 45 |  | Jetted our line in front of home our line was partially obstructed. | Windham | 25 Chapman St, Windham, CT
45

## WINSTED
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
WINSTED WPCF | Closed | Sewage Bypass | Dry | 2022-06-24 | 11:15 AM | Lateral - Public | Raw Sewage | Other | Eversource pole digger hit low pressure system lateral. | Eversource contacted public works department. | 500gal | Approximately 10gpm for 45min until shut down by collections. | Yes | Highland Lake | 2022-06-24 | 12:00 PM | 500 gal |  | Lateral repaired with pipe section and compression fittings. | Winchester | 730 Lake Dr, Winchester, CT
500