## SSO SUMMARY
The first two sections count the number of events and volume amounts for each type of Sanitary Sewer Overflow (SSO) for each municipality and in total | [31 empty] | This secion keeps track of the approximate gallons spilled from SSOs by municipality - a combined total of CSOs and SSOs is on the Reached Water Summary Tab
Municipality | # of SSO Events | # of NPDES Permitted Bypasses | # ot TOTAL EVENTS | All Events Total Estimated Gallons | # Reached Water | # Excessive Flows - Storm Event | Volume (gallons) Excessive Flows - Storm Event | # Excessive Flows - Snow Melt | Volume (gallons) Excessive Flows - Snow Melt | # Electrical Equipment Failure | Volume (gallons) Eletrical Equipt Failure | # Mechanical Equipment Failure | Volume (gallons) Mech Equipt Failure | # Other - Sewer Break, Crack or Failure | Volume (gallons) Other - Sewer Break, Crack or Failure | # Other - Contractor or other mechanical | Volume (gallons) Other - Contractor or other mechanical | # Other - Water Main Break | Volume (gallons) Other - Water Main Break | # Sewer Line Blockage - Grease | Volume (gallons) Line Blockage - Grease | # Sewer Line Blockage - Rags | Volume (gallons) Line Blockage - Rags | # Sewer Line Blockage - Roots | Volume (gallons) Line Blockage - Roots | # Sewer Line Blockage - Debris (Bricks, Carts,Silt, etc) | Volume (gallons) Link Bolckage - Debris (Bricks, Carts, Silt, etc) | # Sewer Line Blockage - Other | Volume (gallons) Link Bolckage - Other | # Unknown Cause | Volume (gallons) Unknown Cause | Unnamed Waterbody (gallons) | Avery Brook (gallons) | Bantam River (gallons) | Bass Brook (gallons) | Beaver Brook (gallons) | Bridgeport Harbor / LIS (gallons) | Bristol Detention Pond (gallons) | Bristol Fish & Game Club Pond (gallons) | Bruce Brook (gallons) | Byram River (gallons) | Cedar Creek / LIS (gallons) | Connecticut River (gallons) | Cove River (gallons) | Darien Harbor (gallons) | Deckers Brook (gallons) | Farmington River (gallons) | Folly Brook (gallons) | Goff Brook (gallons) | Goodwives River (gallons) | Great Brook (gallons) | Greenwich Cove / Harbor (gallons0 | Hockanum River (gallons) | Hopeville Pond Brook (gallons) | Housatonic River (gallons) | Island Brook (gallons) | Lime Kiln Brook (gallons) | Little River (gallons) | Long Island Sound (gallons) | Mattabassett River (gallons) | Mill Brook (gallons) | Mill Creek (gallons) | Moosup River (gallons) | Naugatuck River (gallons) | New Haven Harbor (gallons) | Norwalk River (gallons) | Old Field Creek (gallons) | Park River (incl N, S & Conduit) (gallons) | Pequabuck River (gallons) | Pequonnock River (gallons) | Piper Brook (gallons) | Quinnebaug River (gallons) | Quinnipiac River (gallons) | Ridgefield Brook (gallons) | Rockhole Brook (gallons) | Rooster River (gallons) | Saugatuck River (gallons) | Shetucket River (gallons) | South Pine Creek Marsh (gallons) | Stony Brook River (gallons) | Thames River (gallons) | Trout Brook (gallons) | Trumpet Brook (gallons) | Two Mile Brook (gallons) | Webster Brook (gallons) | Welton Brook (gallons) | West Branch Lead Mine Brook (gallons) | Willimantic (gallons) | Yellow River (gallons)(gallons)
Ansonia | 2 | 0 | 2 | 156000 | 1 | [6 empty] | 1 | 60000 | [16 empty] | 1 | 96000 | [52 empty] | 60000
Berlin | 4 | 0 | 4 | 2800 | 1 | 2 | 1800 |  |  | 1 | 500 | [10 empty] | 1 | 500 | [36 empty] | 500
Branford | 3 | 0 | 3 | 400 | 1 | [6 empty] | 1 | 200 | [6 empty] | 2 | 200 | [40 empty] | 100
Bloomfield (MDC) | 1 | 0 | 1 | 75 | 0 | 1 | 75
Bridgeport (East & West) | 24 | 38 | 62 | 170228275 | 51 | 38 | 170146000 | [6 empty] | 1 | 1000 | 1 | 78000 |  |  | 17 | 3030 | 3 | 220 |  |  | 1 | 20 | 1 | 5 | [7 empty] | 47290000 |  |  | 540 |  | 122856100 | [13 empty] | 30 | [13 empty] | 50 | [5 empty] | 79000 | [12 empty] | 1050
Bristol | 5 | 0 | 5 | 15075 | 3 | 3 | 15025 | [14 empty] | 1 | 0 | 1 | 50 | [12 empty] | 13000 | 900 | [29 empty] | 1125
Cheshire | 2 | 0 | 2 | 2100000 | 1 | 2 | 2100000 | [65 empty] | 2000000
Cromwell (Mattabassett) | 8 | 0 | 8 | 166019526 | 8 | 8 | 166019526 | [35 empty] | 166019526
Coventry | 1 | 0 | 1 | 15239 | 0 | [24 empty] | 1 | 15239
Danbury | 7 | 0 | 7 | 7490072 | 3 | 3 | 7287000 |  |  | 1 | 40000 | 1 | 3000 | 1 | 160000 | [14 empty] | 1 | 72 | 3000 | [24 empty] | 200000
Darien | 5 | 0 | 5 | 910 | 3 | 1 | 650 | [6 empty] | 1 | 50 | 1 | 135 |  |  | 2 | 75 | [23 empty] | 135 |  |  |  |  | 650 | [29 empty] | 50
Derby | 5 | 0 | 5 | 2008000 | 4 | 4 | 1985000 | [22 empty] | 1 | 23000 | [23 empty] | 1985000
East Hartford (MDC) | 3 | 0 | 3 | 19662075 | 2 | 2 | 19662000 | [22 empty] | 1 | 75 | [39 empty] | 19601000 | [10 empty] | 61000
East Windsor | 2 | 0 | 2 | 0 | 0 | [22 empty] | 2 | 0
Enfield | 2 | 0 | 2 | 85000 | 0 | 1 | 80000 | [6 empty] | 1 | 5000
Fairfield | 5 | 0 | 5 | 19250 | 1 | 3 | 17000 | [6 empty] | 1 | 250 |  |  |  |  | 1 | 2000 | [57 empty] | 250
Farmington | 3 | 0 | 3 | 30500 | 1 |  |  |  |  | 1 | 5000 |  |  | 1 | 25000 | [12 empty] | 1 | 500 |  |  | 25000
Glastonbury | 1 | 0 | 1 | 50000 | 0 | [18 empty] | 1 | 50000
Greenwich | 7 | 0 | 7 | 35270 | 7 | 6 | 35000 | [8 empty] | 1 | 270 | [23 empty] | 9000 | [10 empty] | 26270
Griswold (Jewett City) | 3 | 0 | 3 | 1250 | 2 | 1 | 500 | [20 empty] | 1 | 500 | 1 | 250 | [40 empty] | 750
Groton (City, Town & USN) | 13 | 0 | 13 | 9916 | 3 | [8 empty] | 1 | 9000 |  |  |  |  | 5 | 245 | 1 | 250 |  |  | 1 | 0 | 4 | 401 | 1 | 20
Hamden (GNHWPCA) | 15 | 0 | 15 | 11356 | 2 | [8 empty] | 1 | 50 |  |  |  |  | 5 | 320 | 2 | 4540 | 1 | 5 | 1 | 250 | 1 | 2491 | 4 | 3700
Hartford (MDC) | 69 | 0 | 69 | 75791325 | 32 | 59 | 75665500 |  |  | 1 | 4000 | 1 | 120000 | 1 | 750 |  |  |  |  | 1 | 500 |  |  |  |  | 4 | 425 |  |  | 2 | 150 |  |  |  | 20000 | 20000 | [6 empty] | 40000 |  |  | 90000 |  | 40750 | 20000 | [11 empty] | 500 | [6 empty] | 20950 |  |  | 28398000 | [10 empty] | 45645000 |  |  | 906000
Killingly | 2 | 0 | 2 | 2050 | 0 |  |  |  |  | 2 | 2050
Litchfield | 3 | 0 | 3 | 2600045 | 1 | 1 | 2600000 | [6 empty] | 1 | 25 | [10 empty] | 1 | 20 | [6 empty] | 2600000
Manchester | 2 | 0 | 2 | 1611 | 1 | [6 empty] | 1 | 561 | [8 empty] | 1 | 1050 | [29 empty] | 1050
Mansfield (UCONN) | 2 | 0 | 2 | 384000 | 0 | 1 | 380000 | [6 empty] | 1 | 4000
Meriden | 3 | 0 | 3 | 991375 | 1 | 2 | 990075 | [12 empty] | 1 | 1300 | [51 empty] | 990000
Middletown | 1 | 0 | 1 | 30 | 0 | [24 empty] | 1 | 30
Milford | 6 | 0 | 6 | 23030 | 2 | 3 | 13000 | [6 empty] | 1 | 10000 | [14 empty] | 2 | 30 | [23 empty] | 13000
Montville | 3 | 0 | 3 | 76000 | 1 | 1 | 75000 | [6 empty] | 2 | 1000 | [65 empty] | 75000
Naugatuck | 4 | 0 | 4 | 68950 | 1 | 1 | 67500 | [6 empty] | 1 | 300 | [6 empty] | 1 | 750 |  |  | 1 | 400 | [36 empty] | 67800
New Haven (GNHWPCA) | 4 | 65 | 69 | 294491520 | 66 | 66 | 294485900 | [10 empty] | 1 | 3500 | 2 | 2120
New London | 4 | 0 | 4 | 20073 | 3 | [6 empty] | 2 | 200 | 2 | 19873 | [65 empty] | 19973
New Milford | 1 | 0 | 1 | 1625 | 1 | [20 empty] | 1 | 1625 | [23 empty] | 1625
Newington (MDC) | 26 | 0 | 26 | 64171315 | 8 | 24 | 64171235 | [22 empty] | 2 | 80 |  |  |  |  | 40000 | [34 empty] | 62964000 |  |  |  | 40000 | [6 empty] | 1126000
Newtown | 1 | 0 | 1 | 0 | 0 | [6 empty] | 1 | 0
North Haven | 1 | 0 | 1 | 50 | 0 | [20 empty] | 1 | 50
Norwalk | 12 | 0 | 12 | 14840 | 2 | 4 | 8525 |  |  |  |  | 2 | 5075 | [6 empty] | 2 | 60 |  |  |  |  | 4 | 1180 | [38 empty] | 8000
Norwich | 11 |  | 11 | 478547 | 6 |  |  |  |  | 2 | 32202 | 1 | 4404 | 2 | 377952 | 1 | 48206 |  |  | 1 | 15581 | 2 | 200 | [6 empty] | 2 | 2 | [46 empty] | 19985 |  |  | 430055
Oxford | 2 | 0 | 2 | 90000 | 2 | [8 empty] | 2 | 90000 | [42 empty] | 90000
Plainfield | 2 | 0 | 2 | 1190400 | 1 | 1 | 1190000 | [18 empty] | 1 | 400 | [35 empty] | 1190000
Plymouth | 1 | 0 | 1 | 500 | 0 | [8 empty] | 1 | 500
Portland | 1 | 0 | 1 | 225000 | 0 | [6 empty] | 1 | 225000
Ridgefield | 3 | 0 | 3 | 550 | 1 | [6 empty] | 1 | 100 |  |  | 1 | 200 |  |  | 1 | 250 | [52 empty] | 250
Rocky Hill | 1 | 0 | 1 | 900 | 1 | 1 | 900 | [35 empty] | 900
Simsbury | 4 | 0 | 4 | 1200 | 2 | [14 empty] | 2 | 900 |  |  | 2 | 300 | [21 empty] | 300
South Windsor | 5 | 0 | 5 | 134300 | 4 |  |  |  |  | 4 | 134270 | [14 empty] | 1 | 30 | [5 empty] | 28000 | [9 empty] | 106270
Southbury | 2 | 0 | 2 | 40 | 0 | [8 empty] | 2 | 40
Southington | 9 | 0 | 9 | 309729 | 3 | 3 | 309400 | [8 empty] | 1 | 2 |  |  | 3 | 202 |  |  |  |  | 2 | 125 | [45 empty] | 309400
Stafford | 2 | 0 | 2 | 432375 | 2 | 2 | 432375 | [80 empty] | 432375
Stamford | 4 | 0 | 4 | 15798 | 1 | [8 empty] | 2 | 768 | 2 | 15030 | [41 empty] | 15000
Stonington | 3 | 0 | 3 | 25250 | 0 | [6 empty] | 1 | 50 | 1 | 25000 | 1 | 200
Stratford | 5 | 0 | 5 | 26127240 | 5 | 4 | 25830000 |  |  | 1 | 297240 | [43 empty] | 26127240
Suffield | 2 | 0 | 2 | 2287000 | 2 | 2 | 2287000 | [35 empty] | 2287000
Thomaston | 1 | 0 | 1 | 75 | 1 | [10 empty] | 1 | 75 | [46 empty] | 75
Torrington | 8 | 0 | 8 | 23188735 | 7 | 7 | 23188235 |  |  | 1 | 500 | [52 empty] | 23187610 | [22 empty] | 625
Trumbull | 5 | 0 | 5 | 8480 | 2 | [6 empty] | 1 | 2500 | 4 | 5980 | [16 empty] | 2850 | [37 empty] | 2500
Vernon | 2 | 0 | 2 | 55550 | 1 |  |  |  |  | 1 | 55500 | [10 empty] | 1 | 50 | [29 empty] | 55500
Wallingford | 3 | 0 | 3 | 7620 | 0 | 3 | 7620
Waterbury | 8 | 1 | 9 | 138425 | 7 | 3 | 113000 | [8 empty] | 1 | 12000 |  |  |  |  | 1 | 20 | 1 | 30 |  |  | 2 | 5075 | 1 | 8300 | [22 empty] | 4800 | [9 empty] | 118575 | [18 empty] | 12000 |  |  | 3000
West Haven | 17 | 0 | 17 | 609710 | 10 | 6 | 605000 |  |  |  |  | 5 | 1750 |  |  | 1 | 500 | 1 | 2000 | 3 | 360 | [6 empty] | 1 | 100 | [14 empty] | 565500 | [14 empty] | 15200 | [5 empty] | 2000 |  | 25750
West Hartford (MDC) | 96 | 0 | 96 | 58042340 | 32 | 76 | 55789925 |  |  |  |  | 1 | 50 | 9 | 2238825 |  |  |  |  | 4 | 325 | 1 | 20 | 1 | 75 | 3 | 13075 | 1 | 45 | [13 empty] | 20075 | [9 empty] | 5000 | [7 empty] | 150 | [6 empty] | 20000 |  |  | 41916075 | [10 empty] | 13555075 |  |  | 274500
Westport | 7 | 0 | 7 | 3585 | 2 |  |  |  |  | 1 | 500 | 2 | 185 | 3 | 2400 | [12 empty] | 1 | 500 | [47 empty] | 500 |  |  | 2000
Wethersfield (MDC) | 17 | 0 | 17 | 21816097 | 7 | 6 | 21815000 |  |  |  |  | 1 | 75 | 2 | 78 |  |  |  |  | 1 | 750 | 1 | 10 |  |  | 1 | 75 | 4 | 34 | 1 | 75 | [15 empty] | 75 | [23 empty] | 16036000 | [10 empty] | 5789000 |  |  | 270000
Windsor (MDC) | 13 | 0 | 13 | 81283992 | 7 | 6 | 81228150 | [6 empty] | 1 | 10000 |  |  |  |  | 2 | 825 | [6 empty] | 2 | 5007 | 2 | 40010 | [15 empty] | 352400 | [23 empty] | 23655000 |  |  |  | 40000 | [6 empty] | 57220750
SUMMARY | 499 | 104 | 603 | 1023052266 | 319 | 357 | 1018602916 | 0 | 0 | 16 | 571762 | 24 | 423150 | 46 | 2987841 | 12 | 154618 | 2 | 5500 | 55 | 29043 | 16 | 7610 | 7 | 50460 | 23 | 17675 | 21 | 14658 | 24 | 187033 | 30850 | 28000 | 2600000 | 20000 | 60000 | 47290000 | 13000 | 900 | 540 | 9000 | 122856100 | 168473771 | 565500 | 135 | 90000 | 352775 | 40750 | 20000 | 650 | 1625 | 26270 | 61550 | 4800 | 28125240 | 30 | 200000 | 90000 | 30200 | 500 | 650 | 100 | 1190000 | 23374060 | 2000 | 8000 | 25750 | 40950 | 1125 | 2550 | 192570075 | 750 | 3299400 | 250 | 80000 | 79000 | 500 | 19985 | 250 | 2050 | 525028 | 123396825 | 12000 | 60000 | 1450500 | 3000 | 625 | 432375 | 1050
[6 empty] | 603 | 1023052266
[32 empty] | TOTAL REACHED WATER: |  | 717571034
Data Caveats
While DEEP is the storehouse for the SRTK data, DEEP makes the following caveats:
· All data is submitted by publicly owned wastewater treatment plants and publicly owned satellite collection systems.
· DEEP does not issue notifications about individual discharges, they are inputted by the reporters for each municipality and issued by the electronic system automatically.
· The reports are being submitted by the municipalities in a short time frame after discovery of a discharge and specific details may not be known.
· Data is estimated based on the existing systems, models, and personal knowledge of the sewer systems by the reporters.
· Data quality, especially volumes, is not checked by DEEP.
· The electronic program allows for zero duration, short durations and zero quantities for volumes.
· Addresses may not be entered by municipalities in a way that allows the parts of the address to be separated nor with an exact location.
· Multiple notifications may be sent for the same discharge since municipalities need to submit daily and termination reports for ongoing discharges.
· Duplicate reports and reports submitted that resulted in zero flow may be rescinded in the system.

## ANSONIA
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
ANSONIA | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-19 | 07:00 AM | Pump Station | Raw Sewage | Other | Heavy rain event pump station is in a high I&I area. Both pumps were keeping up just at a higher tha | During heavy rain events I check all pump stations it was discovered during my check. Auto dialer wa | 96,000 gallons | 800 GPM from bypass pump and the pump hour meter went up by 2 hours | No |  | 2023-12-20 | 09:00 AM | 96,000 gallons | 96000 |  | Pumps stayed on line and eventually went back to normal wet well levels and bypass system was turned | Ansonia | 19 Glen Dr, Ansonia, CT
ANSONIA | Closed | Sewage Bypass | Dry | 2023-08-22 | 03:45 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | mechanical or electrical i am still trying to find that out | autodialer | 6000 gallons | by manufacturers pump specs by by pass pumping rates and recent upgrade with VFD's we got a more acc | Yes | twomile brook | 2023-08-24 | 04:30 PM | 6000 gallons (estimate) | 60000 |  | bypass pumps pumped down the well to reach the stations submersible pumps. once we got down low enou | Ansonia | 19 Glen Dr, Ansonia, CT
[17 empty] | TOTAL VOLUME | 156000

## BERLIN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BERLIN WATER CONTROL | Closed | Sewage Bypass | Dry | 2023-12-29 | 10:30AM | Pump Station | Raw Sewage | Electrical Equipment Failure | Pump failure required draining wet well to repair pumps | routine visit | approx. 500 gallons | by pumping time | Yes | Mattabassett River | 2023-12-29 | 04:00 PM | 500 | 500 | approx. based on vac truck bein used | power and pump restored | Berlin | 634 Deming Rd, Berlin, CT
KENSINGTON FIRE DISTRICT | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-28 | 06:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags |  | Visual observation | 500 gallons | Visual observation | No |  | 2023-12-28 | 11:00 AM | 500 gallons | 500 |  |  | Berlin | 384 Main St, Berlin, CT
KENSINGTON FIRE DISTRICT | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-18 | 07:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Morning rounds | 800 gallons | Visuale op | No |  | 2023-12-19 | 07:00 AM | 800 gallons | 800 |  | Rain stopped | Berlin | 36 Upson Ave, Berlin, CT
KENSINGTON FIRE DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-03-14 | 07:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Flooding onto street from manhole cover | 1000 gallons | Visual estimation of apparent rate and best guess of storm end time, may update as storm still ongoi | No |  | 2023-03-14 | 11:00 PM | 1000 gallons | 1000 |  | They report that they shut down two pumps to force less water into surcharged pipes. | Berlin | 319 New Britain Rd, Berlin, CT
[17 empty] | TOTAL VOLUME | 2800

## BRANFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRANFORD | Closed | Sewage Bypass | Dry | 2023-12-11 | 12:00 PM | Manhole | Raw Sewage | Mechanical Equipment Failure | one of the three pumps became clogged | resident called the W.P.C. OFFICE | 200 gallons of sewage . | visual | No |  | 2023-12-11 | 01:30 PM | 200 gallons | 200 |  |  | Branford | 31 Damascus Rd, Branford, CT
BRANFORD | Closed | Sewage Bypass | Dry | 2023-11-15 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | resident called the W.P.C.F. | 100 | VISUAL | No |  | 2023-11-15 | 10:45 AM | 100 gallons | 100 |  | jet sewer line | Branford | 116 N Main St, Branford, CT
BRANFORD | Closed | Sewage Bypass | Dry | 2023-09-04 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease build up in sewer line | Resident | 100 gallons | Visual observation | Yes | Mill Creek | 2023-09-04 | 12:30 PM | 100 gallons of sewage. | 100 |  | Jet truck jetted sewer line | Branford | Driscoll Rd, Branford, CT
[17 empty] | TOTAL VOLUME | 400
NOT COUNTED _ NO BYPASS OCCURRED
BRANFORD | Closed | Sewage Bypass | Dry | 2023-04-24 | 08:00 AM | Pump Station | Raw Sewage | Other | installing new base and elbow and new force main in wet well for number one pump at Hosley pumpstati | the number one pump's base broke and the elbow snaped off . | there was no discharge to the ground the number two pump handled the flow . |  | No |  | 2023-04-24 | 01:00 PM | 0 gallons | 0 |  |  | Branford | 250 Hosley Ave, Branford, CT

## BRIDGEPORT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-28 | 04:45 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | Heavy rain fall / High flows | Street level indicator / flow meter | N/A | N/a | Yes | Bridgeport Harbor / Long Island Sound | 2023-12-28 | 11:00 AM | 3.49mg | 3490000 |  | Rain event ended. | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-12-18 | 04:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Street level indicator and flow meter | 6.03mg. | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-12-18 | 05:00 PM | 6.03mg | 6030000 |  | Heavy rain ended and plant resumed normal operation. | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-12-10 | 03:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Street level indicator and flow meter | NA | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-12-11 | 09:00 AM | 8.3mg. | 8300000 |  | rain ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-11-22 | 04:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy Rain / High Flows | Flow meter / street level indicator | N/A | N/A | Yes | Bridgeport Harbor / Long Island Sound | 2023-11-22 | 10:30AM | 3.33 MG | 3330000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-09-29 | 06:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Street level indicator and flow meter. | 10.13 mg | Flow meter | Yes | Bridgeport Harbor / Long Island Sound. | 2023-09-30 | 03:00 AM | 10.13mg. | 10130000 |  | heavy rain ended. plant resumed normal operation | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-09-18 | 08:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | high flows due to heavy rain | Street level indicator and flow meter | .94mg. | flow meter | Yes | Bridgeport Harbor/ Long Island Sound | 2023-09-18 | 10:45 PM | .94mg. | 940000 |  | rain ended and high flows decreased. | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-09-13 | 04:30 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain / High flows | Flow meter / High Flows | .62 MGD | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-09-13 | 05:45 AM | .62 MGD | 620000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-10 | 01:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain / high flows | Flow meter / street level indicator | 1.37 MGD | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-09-10 | 04:30 AM | 1.37 MGD | 1370000 |  | Rain event ended. | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-08-18 | 06:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Flow meter and street level indicator | 1.85 MGD | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-08-18 | 10:00 AM | 1.85 MGD | 1850000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-05-20 | 01:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain / high flow | Flow meter/ street level indicator | 5.32 mg | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-05-21 | 00:00 AM | 5.32 mg | 5320000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-28 | 04:00 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | Rain event | street level indicator | N/A | N/A | Yes | cedar creek / long Island Sound | 2023-12-28 | 01:00 AM | 5.51 MG | 5510000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-18 | 03:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Observation | 11.1 MG | Flow totalizer | Yes | Cedar Creek Long Island Sound | 2023-12-18 | 09:00 PM | 11.1 MG | 11100000 |  | Storm Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-10 | 02:30 PM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event |  | observation | N/A |  | Yes | cedar creek long island sound | 2023-12-11 | 12:15 PM | 13.3 MGD | 13300000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-11-22 | 03:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2023-11-22 | 02:00 PM | 7.29 MGD | 7290000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2023-10-29 | 02:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2023-10-29 | 05:15 PM | 1.62 MGD | 1620000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-30 | 09:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain fall | visual observation / street level indicator | N/A | N/A | Yes | Long Island Sound / Cedar Creek | 2023-09-30 | 02:00 PM | 3.16 MGD | 3160000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-29 | 03:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual observation | N/A | N/A | Yes | Long Island Sound Cedar Creek | 2023-09-30 | 03:45 AM | 18.4 mgd | 18400000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-18 | 01:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | N/A | N/A | Yes | Long Island Sound Cedar Creek | 2023-09-18 | 05:45 PM | 5.2 mgd | 5200000 |  | Event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-08-18 | 06:45 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Flow meter and street level indicator | N/A | N/A | Yes | Cedar Creek / Long Island Sound | 2023-08-18 | 11:30 AM | 6.49 MG | 6490000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-25 | 09:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Street level indicator | 5.4 mg | Flow meter | Yes | Cedar Creek / Long Island Sound | 2023-01-26 | 12:00 PM | 5.4mg | 5400000 |  | Heavy rain ended and street level was back in range. | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-12-20 | 04:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | N/A | Homeowner notified Bridgeport WPCA by phone. | N/A | N/A | No | N/A | 2023-12-20 | 06:00 AM | N/A | 20 |  | Field operations staff jetted the main line and cleared it of any debris. | Bridgeport | 165 Jewett Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-09-22 | 12:30 PM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | Contractor damaged line | Contractor notified water company who then contacted Bridgeport WPCA | 78,000 gallons | Volume Calculator | Yes | Rooster River | 2023-09-22 | 03:15 PM | 78,000 gallons | 78000 |  | Contractor repaired line | Bridgeport | 3870 Park Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-08-15 | 03:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain | Flow meter and street level indicator | N/A | flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-08-15 | 07:00 AM | 1.6mg. | 1600000 |  | Rain event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-07-27 | 07:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Street level indicator. and high flow. | 0.51 mg. | Flow meter | Yes | Bridgeport Harbor/ long Island Sound | 2023-07-27 | 08:15 PM | 0.51mg. | 510000 |  | Rain subsided and plant resumed normal operations | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-07-04 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | heavy rain | high flows, street level indicator | 1.63mg. | Flow meter | Yes | Bridgeport Harbor/ Long Island Sound | 2023-07-04 | 09:00 PM | 1.63mg. | 1630000 |  | rain event ended and plant resumed normal operations | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-07-03 | 11:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain | Street level indicator | 2.17mg. | Flow meter | Yes | Bridgeport Harbor / Long Island Sound | 2023-07-04 | 03:45 AM | 2.17mg. | 2170000 |  | Rain ended and plant resumed normal operations | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-06-16 | 05:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | rags, roots and a hair weave | Home owner notified the Bridgeport WPCA | N/A personnel not permitted to enter private residence | N/A | No |  | 2023-06-16 | 05:45 PM | N/A Personnel not permitted to enter private residence | 20 |  | Line was jetted and clog was cleared | Bridgeport | 660 William St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-06-11 | 02:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and roots | Homeowner notified the WPCA | N/A | N/A | No |  | 2023-06-11 | 03:45 PM | N/A Personnel not permitted to enter private residence | 20 |  | Main line was jetted and clog was cleared. | Bridgeport | 1068 State St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-05-10 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags | Inframark road crew employee driving past the manhole discovered the problem | 30 gallons | visual determination | Yes | Island Brook | 2023-05-10 | 11:00 AM | 30 gallons | 30 |  | Staff cleared the clogged main line using a jetter truck. | Bridgeport | 251 North Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-04-06 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | N/A | Homeowner notified the Bridgeport WPCA | 20 gallons | Visual determination | Yes | Bruce Brook | 2023-04-06 | 02:45 PM | 20 Gallons | 20 |  | Field Operations Personnel jetted the main line and cleared grease blockage and cleaned area | Bridgeport | 422 Pearl Harbor St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 03:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags | Homeowner in complex discovered sewage in the basement and notified the WPCA. | N/A Personnel not permitted to enter private residence. | N/A Personnel not permitted to enter private residence. | No |  | 2023-03-14 | 05:00 PM | NA Personnel not permitted to enter private residence | 20 |  | Field Operations used a jetter truck to clear blockage and remove grease and rags from the main line | Bridgeport | 40 Sanford Pl, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-03-06 | 12:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease, rags and other debris | The homeowner at 223 Pearl Harbor Street notified the Bridgeport WPCA of a sewage bypass at a manhol | 300 gallons | Visual determination | Yes | Bruce Brook | 2023-03-06 | 01:00 PM | 300 gallons | 300 |  | Field Operations personnel jetted the main line and removed rags , grease and other debris. Cleaned | Bridgeport | 181 Wessels Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-03-05 | 05:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | N/A | Homeowner discovered sewage in their basement and notified the WPCA | N/A | N/A Staff not permitted to enter private residence | No |  | 2023-03-05 | 08:30 PM | N/A Staff not permitted to enter private residence | 20 |  | Field operations removed a substantial amount of grease from the main line. | Bridgeport | 259 Beach St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-02-24 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Home Owner notified the Bridgeport WPCA | NA |  | Yes | Bruce Brook | 2023-02-24 | 12:00 PM | NA | 100 |  | Staff jetted the main line and cleared clog. | Bridgeport | 303 Pearl Harbor St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-02-21 | 03:45 PM | Lateral - Public | Raw Sewage | Sewage Line Blockage - Rags | Rags and hair weave | Board of Education notified WPCA | 100 gallons | visual | No | NA | 2023-02-21 | 05:00 PM | 100 gallons | 100 |  | Jetted main line . cleared blockage and removed debris. Cleaned area | Bridgeport | 432 Fairview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-02-07 | 09:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Combination of grease and rags. | Homeowner notified the Bridgeport WPCA | 100 gallons | visual determination | Yes | Bruce Brook / Bruce Pond | 2023-02-07 | 10:30AM | 100 Gallons | 100 |  | Field Operations personnel jetted the main line and cleared blockage of rags and grease. | Bridgeport | 31 Sage Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2023-01-18 | 08:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Water company notified the Bridgeport WPCA | N/A unknown |  | Yes | Long Island Sound | 2023-01-18 | 10:00 PM | Unknown | 100 |  | Field Operations personnel jetted the main line and cleared grease blockage. | Bridgeport | E Main St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-12-11 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by Police Department | 1000 Gals | Visual Observation | Yes | Bunneils Pond | 2023-12-11 | 04:00 PM | 1000 Gals | 1000 |  | Main Line cleaned | Bridgeport | 1680 Reservoir Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-08-15 | 04:30 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | Cedar Creek / Long Island Sound | 2023-08-15 | 07:30 AM | 2.07 MGD | 2070000 |  | Rain event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-08-07 | 09:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2023-08-07 | 01:00 PM | 2.7 MGD | 2700000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-08-03 | 12:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by homeowner | N/A | N/A | No |  | 2023-08-03 | 01:45 PM | N/A | 50 |  | Main Line was jetted and cleared | Bridgeport | 25 Sunshine Cir, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-07-27 | 09:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | n/a | n/a | Yes | Cedar Creek / Long Island Sound | 2023-07-27 | 00:00 AM | 2.14 MGD | 2140000 |  | Event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-18 | 03:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | N/A | N/A | Yes | Long Island Sound Cedar Creek | 2023-07-18 | 06:45 PM | 2.17 MG | 2170000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-16 | 10:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  |  | N/A | N/A | Yes | Cedar Creek Long Island Sound | 2023-07-16 | 05:45 PM | 4.6 MG | 4600000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-04 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | 4.76 MG | Flow Totalizer | Yes | Cedar Creek Long Island Sound | 2023-07-05 | 01:00 AM | 4.76 MG | 476000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-03 | 10:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | 5.7 MG | Flow Totalizer | Yes | Long Island Sound Cedar Creek | 2023-07-04 | 06:00 AM | 5.7 MG | 5700000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-06-26 | 11:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | main line that was clogged Rocks and Wipes | Resident Call In | 5 Gal | Visual Estimate | No |  | 2023-06-26 | 01:30 PM | 5 gals | 5 |  | line was cleared | Bridgeport | 40 Infield St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-05-20 | 12:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | unknown | N/A | Yes | Long Island Sound Cedar Creek | 2023-06-21 | 00:45 AM | 9.1 mg | 9100000 |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-05-19 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Call in by resident | Unknown | Unknown | No |  | 2023-05-19 | 11:30 AM | Unknown | 50 |  | Main line cleared. | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-05-03 | 10:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Main Line Blocked with Grease and Rags | Called in by business owner | 20 gals | estimated | Yes | Bruce Brook | 2023-05-03 | 10:30AM | 20 Gals | 20 |  | Jetted sewer line | Bridgeport | 1905 Barnum Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-04-30 | 05:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual | Unknown | N/A | Yes | Cedar Creek Long Island Sound | 2023-04-30 | 11:00 PM | 4.59 MGD | 4590000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-04-29 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual observation | unknown | N/A | Yes | Cedar Creek Long Island Sound | 2023-04-29 | 11:00 PM | 3.66 MGD | 3660000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-04-29 | 07:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | unknown | N/A | Yes | Cedar Creek Long Island Sound | 2023-04-29 | 11:00 AM | 3.18 MGD | 3180000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-04-23 | 05:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Storm | Visual Observation | unknown | unknown | Yes | Long island sound cedar creek | 2023-04-23 | 06:30 AM | 0.7 MGD | 700000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-04-07 | 09:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Visual observation | 20 gals | visual | Yes | Pequannock River | 2023-04-07 | 10:45 AM | Unknown | 50 |  | Line cleared | Bridgeport | 1065 Housatonic Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-03-15 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease | Visual Observation | 1000 Gal | Visual | Yes | Yellow Mill River | 2023-03-15 | 11:30 AM | 1000 Gals | 1000 |  | Main line jetted and cleared | Bridgeport | Pearl Harbor St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-03-02 | 04:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Grease Blockage | Resident Email to WPCA | Unknown | Unknown | Yes | Yellow Mill River | 2023-03-02 | 07:30 PM | Unknown | 50 |  | Main Line cleaned of debris and grease | Bridgeport | 147 Priscilla St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-01-28 | 05:45 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Visual | unknown | Unknown | Yes | Rooster River | 2023-01-29 | 02:00 AM | 1000 Gals | 1000 |  | Force main Repaired | Bridgeport | 187 Ardmore St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-23 | 01:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual | unknown | unknown | Yes | Cedar creek long island sound | 2023-01-23 | 06:30 AM | 1.7 MG | 1700000 |  | Event ended. | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-01-20 | 03:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Inframark employees while in route the shop, noticed raw sewage coming out of a man hole at East Mai | 100 gals | Visual | No |  | 2023-01-20 | 05:15PM | 100 Gals | 100 |  | Event ended. | Bridgeport | E Main St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2023-01-20 | 05:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Inframark employees while in route the shop, noticed raw sewage coming out of a manhole at 248 Salem | Visual | 58 gals | visual | No |  | 2023-01-20 | 05:30 PM | 100 Gals | 100 |  | Event ended. | Bridgeport | 248 Salem St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-19 | 10:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual Observation | 2.6 MG | Flow Totalizer | Yes | Long Island Sound Cedar Creek | 2023-01-20 | 03:30 AM | 2.6 MG | 2600000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
[17 empty] | TOTAL VOLUME | 170228275

## BRISTOL
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-18 | 01:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Visual inspection of Memorial Boulevard | 15-20gpm. | 5 gallon bucket test. | Yes | City of Bristol Detention Pond Memorial Boulevard | 2023-12-18 | 11:00 PM | 12,000-15,000 gallons. | 13000 | calculated based on initial observation | time allowed collection system to become not surcharged. | Bristol | 424 South St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 10:15 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy Rains in a short amount of time caused a spike in flow. The UV channel high float tripped shut | Plant Operator observed that the UV's shut off and saw the high float alarm. | 1,125,000 Gallons. | Calculation based off flow and time. | Yes | Pequabuck River | 2023-07-16 | 11:00 AM | 1,125,000 Gallons. | 1125 |  | A secondary channel at the Outfall was partially opened and the UV channel Dam gate was adjusted. | Bristol | 75 Battisto Rd, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 09:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Storm event Sunday morning July 16th was the cause of the bypass. Staff discovered signs of a bypass | Quantity unknown. Estimate less than 1000 gallons. | Based on time frame of discharge and debris around the manhole that it was less than 1000 gallons. | Yes | Bristol Fish and Game club pond | 2023-07-16 | 11:30 AM | Unknown. believed to be less than 1000 gallons. | 900 |  | SSO stopped after storm event and flow subsided. | Bristol | 456 South St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2023-05-05 | 09:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Roots | Roots in line at 45 feet. | Received call from resident at 57 Driscoll Street | 50 gallons. Discharging out of residents clean out at 46 Driscoll Drive. | Based on amount discharging out of clean out at 48 Driscoll Drive. | No |  | 2023-05-05 | 11:00 AM | 50 Gallons | 50 |  | Line jet cleaned | Bristol | 57 Driscoll Dr, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2023-05-04 | 08:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Build of rags and grease in the sewer main. | Water Department received a call from the homeowner at 39 Douglas Road. Sewage was backing up into b | unknown. | unknown. | No |  | 2023-05-04 | 09:30 AM | unknown. Did not enter the home. | 0 |  |  | Bristol | 39 Douglas Rd, Bristol, CT
[17 empty] | TOTAL VOLUME | 15075

## CHESHIRE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
CHESHIRE | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 07:30 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | river table high and causing 15MGD coming into plant designed for 4MGD | operators on call for storm 24 HR staffed | 200 GPM spilling out into drain system that goes back into headworks | visually best educated guess | No |  | 2023-12-19 | 06:30 AM | 100,000 gallons estimated, all returned back to our influent building from spilling out of the grit | 100000 |  | the flow subsided from the storm, so our grit channel was no longer hydraulically overloaded. | Cheshire | 1325 Cheshire St, Cheshire, CT
CHESHIRE | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-05-01 | 09:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | we diverted 25 % of flow away from phosphorus treatment to keep from overflowing the alum contact ch | We opened the valve 25 % to allow some wastewater to be diverted away from disc filter units | 25 % of the daily flow, which at time looks to be about 7-8 MGD. I would estimate 1.5 MGD - 2 MGD di | math | Yes | Quinnipiac River | 2023-05-02 | 01:00 AM | 1.5 MGD - 2 MGD | 2000000 |  | Stoem ended | Cheshire | 1325 Cheshire St, Cheshire, CT
[17 empty] | TOTAL VOLUME | 2100000

## CROMWELL MATT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-12-28 | 10:30AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 80 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-12-29 | 00:30 AM | 6,241,631 gallons of partially treated effluent, combined with 32,380,648 gallons of fully treated e | 6241631 |  | When plant flows subsided under 55 MGD operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 08:15 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 82 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-12-20 | 02:45 AM | 35,221,808 gallons of partially treated effluent, combined with 97,926,899 gallons of fully treated | 35221808 |  | When plant flows subsided under 55 MGD operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-11 | 02:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 85 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-12-12 | 00:00 AM | 16,517,132 gallons of partially treated effluent, combined with 52,612,840 gallons of fully treated | 16517132 |  | When plant flows subsided under 55 MGD operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 10:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 60 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-10-02 | 01:15 AM | 47,859,167 gallons of disinfected partially treated effluent, combined with 150,376,877 gallons of f | 47859167 |  | When plant flows subsided to 55 MGD operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 08:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate. | Plant influent was approximately 75 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-09-27 | 02:15 AM | 35,040,940 gallons of disinfected partially treated effluent, combined with 96,830,954 gallons of fu | 35040940 |  | When plant flows subsided under 55 MGD operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 01:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator Opened Bypass Gate | 5 MGD going through bypass gate at time of bypass gate opening. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-09-14 | 04:15 AM | 5,734,000 gallons of partially treated effluent, combined with 33,623,672 gallons of fully treated e | 5734000 |  | When plant flows subsided under 55 MGD operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 09:15 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator Opened Bypass Gate | 13 MGD going through bypass gate at time of bypass gate opening. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-03-15 | 04:45 AM | 6,065,076 gallons of partially treated effluent, combined with 45,613,248 gallons of fully treated e | 6065076 |  | When plant flows subsided under 55 MGD operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 03:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | New Britain flows hit 43.33 MGD, Middletown hit 16.68 MGD. | Operator opened bypass gate | Plant influent got up to 87MGD, with 55MGD going through full facility, and about 30 MGD receiving p | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | Connecticut River | 2023-01-27 | 01:30 AM | 13,339,772 gallons of partially treated effluent, combined with 54,234,375 gallons of fully treated | 13339772 |  | When plant flows subsided under 55 MGD operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
[17 empty] | TOTAL VOLUME | 166019526

## COVENTRY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
COVENTRY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-05-07 | 11:00 PM | Treatment Plant | Partially Treated Raw Sewage | Other | Infiltration basin overflowed. | We noticed a tree leaning over the basin Monday 5/8/23. The basin was pretty full but not overflowing | estimated 15,239 gallons over a 2 hour period | Rainfall data shows that it rained from 11 PM Sunday 5/7 into 1 AM Monday 5/8. We had 15,239 gallons | No |  | 2023-05-08 | 01:00 AM | estimated 15,239 gallons | 15239 |  | If there was a bypass it stopped long before we became aware of it. | Coventry | 394 Main St, Coventry, CT
[17 empty] | TOTAL VOLUME | 15239

## DANBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DANBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 11:15 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator on Duty | Estimated bypass is 3.6 MG | Flow meter readings and duration of bypass event | No |  | 2023-12-18 | 11:00 PM | 3.6 MG | 3600000 |  | Storm event ended and flows dropped below treatment capacity of secondary treatment | Danbury | 53A Newtown Rd, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 07:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rains >4" | Operators on Duty | 3.487 MG | Flow meter readings and duration of bypass | No |  | 2023-09-02 | 02:30 PM | 3.487 MG | 3487000 |  | Flows dropped to a level where the Equalization tank could be closed and flows sent through secondar | Danbury | 53A Newtown Rd, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 04:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Flow equalization tank reached capacity at 4pm and bypassed to the disinfection tanks until 6pm. Tot | Operator on Duty | 200,000 | Flow meter reading thru the duration of the bypass | No |  | 2023-07-16 | 06:00 PM | 200,000 | 200000 |  |  | Danbury | 53A Newtown Rd, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2023-05-17 | 04:00 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | SCADA communication failure resulting in loss of screw lift pumps the transfer intermediate tank eff | Operator on duty | 40,000 gallons | flow and duration of bypass | Yes | Limekiln Brook | 2023-05-17 | 04:15 PM | 40,000 gallons | 40000 |  | Started screw lift pumps locally and repaired SCADA communication error | Danbury | 18 Plumtrees Rd, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2023-05-03 | 10:00 PM | Treatment Plant | Raw Sewage | Sewage Line Break, Crack or Failure | 30" influent pipe to the comminution failed | Operator on Duty | 50,000 | Estimated based on loss of flow registered at the raw influent flow meter and duration of bypass | Yes | Lime Kiln Brook | 2023-05-03 | 10:30 PM | 160,000 | 160000 |  | Bypass pumps that were in place for a plant upgrade were started | Danbury | 53 Newtown Rd, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2023-04-12 | 02:00 PM | Lateral - Private | Raw Sewage | Unknown | Private sewer lateral has either collapse or has become blocked with roots or grease | Found by city Public Utilities employee | 1gal per hour | Visual estimate | No |  | 2023-04-15 | 00:00 AM | 72 gal | 72 |  | Home owner made repair | Danbury | 105 West St, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2023-02-08 | 03:00 PM | Manhole | Raw Sewage | Mechanical Equipment Failure | VALVE FAILURE IN MANHOLE. | CALLED IN BY PASSERBY | 25GPM | VISUAL ESTIMATE | Yes | WETLANDS | 2023-02-08 | 08:00 PM | 3000 | 3000 |  | BYPASS WAS ON PRIVATE SEWER FORCEMAIN. FORCEMAIN IS FOR "THE SUMMIT" PROPERTY IN DANBURY,CT. FLOW I | Danbury | 3 Enclave Dr, Danbury, CT
[17 empty] | TOTAL VOLUME | 7490072

## DARIEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DARIEN | Closed | Sewage Bypass | Dry | 2023-12-06 | 10:00 AM | Lateral - Public | Raw Sewage | Other | machinery used in construction of nearby curbing impacted valve box of low pressure sewer lateral ca | Contractor reported damage to town. | 100 to 150 gallons | visual observation | Yes | Darien Harbor | 2023-12-06 | 10:45 | 135 gallons | 135 | 3 gal/min, 45 min, = 135 gal, contained and collected. | broken lateral repaired | Darien | 28 Long Neck Point Rd, Darien, CT
DARIEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 05:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Police called Sewer Department | 3 gallons per minute | Visual | Yes | Goodwives River | 2023-09-29 | 10:30 PM | 650 gallons | 650 |  | flow subsided after storm subsided. | Darien | 2 Sedgewick Village Ln, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2023-09-02 | 12:30 PM | Select... | Raw Sewage | Sewage Line Blockage - Other | sedimentation in siphon | resident called in wetness on pavement | 50 gallons | guess | Yes | Stony Brook River | 2023-09-02 | 01:00 PM | 50 gallons | 50 |  | vactor and jet road clean of pipe and post clearance flushing | Darien | 53 Hecker Ave, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2023-08-22 | 00:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | misaligned joint in sewer lateral pipe. Pump. | resident in area reported odor. | 50 gallons | guess. sewage presence inferred. | No | N/A | 2023-08-22 | 00:00 AM | 50 Gallons | 50 |  | Gasket and pipe repair of private lateral by the town | Darien | 51 Buttonwood Ln, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2023-03-17 | 05:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | none | resident noted puddle next to manhole in woods near his house at bottom of hoyt court. | 25 gallons | visual observation of SSO in progress. | No | In Noroton River watershed, but did reach waterbody nor did sewage leave the area | 2023-03-17 | 06:15 PM | 25 gallons | 25 |  | jet rodded from downstream SMH | Darien | 24 Hoyt Ct, Darien, CT
[17 empty] | TOTAL VOLUME | 910

## DERBY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DERBY | Closed | Sewage Bypass | Rain greater than 4" per hour | 2023-12-18 | 08:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | visual | 10 mgd flow for 3 hours. Flow went down below 10 mgd after 11 am | visual and meter readings | Yes | Housatonic river | 2023-12-19 | 00:00 AM | 1.5 million gallons | 1500000 |  | rain event ended and flow came back down below 10 million gallons per day | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2023-11-24 | 03:00 AM | Treatment Plant | Sludge Spill | Other | After the suspect climbed the perimeter fencing and broke into the operations building, he turned on | Upon arrival for work, one of our operators noticed puddling in the front parking lot. Once he enter | 5,000 to 10,000 | visual estimation by the depth in the waste activated sludge tank. | No |  | 2023-11-24 | 12:00 PM | Two-three thousand gallons | 23000 | Visual from return activated sludge in the parking lot and depth of waste tank. | Additional operators were called in to vac up sludge spill and apply lime at grassy areas. | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-04 | 05:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy rain fall causing hydraulic overloading at plant. Shortened detention times in final clarifier | Operator was called in for a plant alarm. While onsite, rain fall became very heavy | 50,000 gallons to 100,000 gallons | Visually | Yes | Housatonic River | 2023-07-04 | 08:30 PM | 75,000 - 100,000 | 85000 |  | Heavy rainfall starting around 5 pm lasting approximately 15 min. Plant inflow receded enough around | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-01-26 | 04:30 AM | Treatment Plant | Sludge Spill | Excessive Flows - Storm Event | Storm event causing high flows | Plant operator called in for high wet well level | 100,000 - 250,000 gallons | Visually | Yes | Housatonic River | 2023-01-26 | 08:15 AM | 100,000 - 250,000 gallons | 200000 |  | Due to the excessive flow coming into the plant our final clarifiers become overloaded causing our s | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-01-26 | 04:30 AM | Treatment Plant | Sludge Spill | Excessive Flows - Storm Event | Storm event causing high flows | Plant operator called in for high wet well level | 100,000 - 250,000 gallons | Visually | Yes | Housatonic River | 2023-01-26 | 08:15 AM | 100,000 - 250,000 gallons | 200000 |  | Due to the excessive flow coming into the plant our final clarifiers become overloaded causing our s | Derby | 1 Caroline St, Derby, CT
[17 empty] | TOTAL VOLUME | 2008000

## EAST WINDSOR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
EAST WINDSOR WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-05-01 | 07:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | Main Sewer has points of off-set joints, root and debris possibly collected at such point. | Home owner called facility. | N/A | Home owner description. Facility Operator Feedback. | No |  | 2023-05-01 | 09:30 AM | NA | 0 |  | Jet Flushed by WPCF Staff | East Windsor | 28 Pleasant St, East Windsor, CT
EAST WINDSOR WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-05-01 | 07:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | Main Sewer line shows signs of off-set joints, roots and grease may have contributed to issue. | Home owner at 28 Pleasant Street contacted facility. | N/A | Home owner description and operator feedback. | No |  | 2023-05-01 | 09:30 AM | N/A | 0 |  | Main Line Jet Flushed | East Windsor | 28 Pleasant St, East Windsor, CT
[17 empty] | TOTAL VOLUME | 0

## ENFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
ENFIELD POTW | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 04:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Called in by police dispatch | 100 gpm - 200 gpm | Visual estimate | No |  | 2023-09-30 | 02:30 AM | between 50,000 - 100,000 gallons | 80000 |  | Heavy Rains subsided | Enfield | 120 Prospect St, Enfield, CT
ENFIELD POTW | Closed | Sewage Bypass | Dry | 2023-05-15 | 04:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | 58 year old transite force main | Called in by a pedestrian | Approximately 5000 gallons | Estimated | No | Freshwater Brook | 2023-05-15 | 04:15 AM | Approximately 5000 gallons | 5000 |  | Yes | Enfield | US-5, Enfield, CT
[17 empty] | TOTAL VOLUME | 85000

## FAIRFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 10:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Storm event | Storm event inspections | 5000 gallons | visual estimate | No |  | 2023-12-19 | 07:00 AM | 5000 gallons | 5000 |  | rain event ended | Fairfield | 129 Halley Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-11 | 03:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | rain event inspections | 5000 Gallons | visual estimate | No |  | 2023-12-12 | 07:00 AM | 5000 Gallons | 5000 |  | storm ended | Fairfield | 129 Halley Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 08:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Inspections during storm event |  |  | No |  | 2023-09-30 | 04:30 AM | 7000 gallons | 7000 |  | storm ended | Fairfield | 122 Halley Ave, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2023-09-21 | 03:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Broken sewer main line | report of a plugged line | 250 gallons | visual estimate | Yes | south pine creek marsh | 2023-09-22 | 01:30 AM | 250 gallons | 250 |  | dig road to replace broken section of pipe during which we had a septage hauler sucking out all flow | Fairfield | 233 Beaumont St, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-30 | 07:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | grease , rags and small tree twigs removed from line | Call from fairfield pd | 2000 gallons total from four locations | visual estimate | No |  | 2023-04-30 | 08:00 PM | 2000 gallons | 2000 |  | jet line to break the plug | Fairfield | 55 Roseville St, Fairfield, CT
[17 empty] | TOTAL VOLUME | 19250

## FARMINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
FARMINGTON | Closed | Sewage Bypass | Dry | 2023-09-01 | 11:30 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | Backup (UPS) circuit board failed, causing the I & C cabinet to lose power. All station and pump co | Call from resident that sewage was coming out of wet well manhole. | Under 5,000 gallons | Response time was around 10 minutes, pumps run approx. 700-1200 gpm when online. Operators put stati | No |  | 2023-09-01 | 11:45 AM' | Under 5,000 gallons | 5000 |  | Critical spare backup was installed. | Farmington | 7 Johnson Ave, Farmington, CT
FARMINGTON | Closed | Sewage Bypass | Dry | 2023-03-22 | 10:30AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Compaction and Material Fail (piercing 14 inch force main pipe) | Checking pump stations, seeing water/sewage on side of roadway. | 100 gpm. | Fill rate of 5 gallon buckets over time. | Yes | Small irrigation ditch and/or (unnamed stream) on the side of 84/Route 4 connector, does not appear | 2023-03-22 | 09:00 PM | Approx. 25,000 gallons. | 25000 |  | 6 foot section of Force Main pipe was replaced (pictures attached). | Farmington | 38 Patrick H Flood Rd, Farmington, CT
FARMINGTON | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-01 | 08:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Brick found in sewer line, possible construction debris. | Homeowner called reporting backup in bathroom, WPCF responded in less than an hour and Vacc'd/jetted | Minimal - less than 500 gallons. | Using estimated flow from area at time of day. | No |  | 2023-01-01 | 10:15 PM | 500 Gallons | 500 |  | Vacc'd/jetted the mainline, locating the brick inside sewer line. | Farmington | 255 Main St, Farmington, CT
[17 empty] | TOTAL VOLUME | 30500

## GLASTONBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GLASTONBURY | Closed | Sewage Bypass | Dry | 2023-07-25 | 12:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots | Root growth in gravity sewer caused force main to overflow first manhole after pump station. | Found by State field worker performing grass mowing. | Difficult to determine when the SSO started, but we know that it happened sometime between Sunday an | Flowmeter at Nutmeg Pump Station | No | none - collected in drainage swale. | 2023-07-25 | 05:30 PM | 8,250 - 66,000 gallons. | 50000 |  | Flushed gravity sewer and removed root ball. | Glastonbury | 105 Nutmeg Ln, Glastonbury, CT
[17 empty] | TOTAL VOLUME | 50000

## GNHWPCA
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-04-09 | 03:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Rags and grease were removed from the line. | Homeowner called it in. | Less than 15 gallons. | Field estimate by crew. | No | N/A | 2023-04-09 | 04:30 PM | Less than 15 gallons. | 13 |  | Crew jetted the city line and restored flow. Pro Klean was contracted to clean and sanitize. | East Haven | 143 Dodge Ave, East Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-11-22 | 08:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Crew observed grease and rags in the line when flow was restored. All material was removed. | Homeowner called it in. | Crew estimated less than 20 gallons were discharged into the basement. | Field estimate by crew. | No | N/A | 2023-11-22 | 09:15 AM | Less than 20 gallons was observed. | 15 |  | Crew jetted the sanitary sewer and restored flow. Pro Klean was contracted to clean and sanitize the | East Haven | 5 Jardin Dr, East Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-12-12 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Reported by property owner in area | less than 100 gallons | Field estimate by road crew | No |  | 2023-12-12 | 11:45 AM' | less than 100 gallons | 80 |  | Line was jetted and flow restored. | East Haven | 371 Short Beach Rd, East Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-12-20 | 02:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage of the sanitary sewer. | Resident called it in. | Less than 100 gallons were discharged to the road surface. | Field estimate by crew. | No | N/A | 2023-12-20 | 04:45 PM | Less than 100 gallons. | 80 |  | Crew jetted the line and restored flow. The road surface was washed down. | East Haven | Foxon Rd, East Haven, CT
188
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-01-15 | 12:30 PM | Basement | Raw Sewage | Unknown | When the crew arrived the sanitary sewer was flowing normal. The crew jetted the line with no change | Resident called it in. | Less than 100 gallons were discharged to the basement. | Field estimate by crew. | No | N/A | 2023-01-15 | 12:45 PM | Less than 100 gallons. | 80 |  | Crew jetted the city line and cleaned the catch basins. Pro Klean was contracted to clean and saniti | Hamden | 145 Shepard Ave, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-02-04 | 04:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | There was a buildup of rags and debris at the intersection of evergreen an Ann’s Farm. The line was | Homeowner called it in. | Less than 50 gallons. | Field estimate by crew. | No | N/A | 2023-02-04 | 04:30 PM | Less than 50 gallons. | 40 |  | Crew jetted the line and removed the debris. Pro Klean was contracted to clean and sanitize. | Hamden | 7 Anns Farm Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-03-04 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | The crew did not determine the cause of the bypass. They believe it was grease. | Homeowner called it in. | 2490 gallons were discharged into the basement. | Basement is 50’x20’ with 4” of water. 50x20x1”(.333’)x7.48=2491 gallons. | No | N/A | 2023-03-04 | 11:45 AM' | 2491 gallons | 2491 |  | Crew jetted the city line and restored flow. Pro Klean was contracted to clean and sanitize. | Hamden | 25 Leo Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-03-04 | 12:15 PM | Manhole | Raw Sewage | Other | Cause is unknown. | RWA called it in. | Less than 100 gallons were discharged from the manhole. | Field estimate by crew. | Yes | Lake Whitney Reservoir After the RWA tested the water in the reservoir, it is inconclusive that effl | 2023-03-04 | 12:15 PM | Less than 100 gallonsAfter the RWA tested the water in the reservoir, it is inconclusive that efflue | 80 |  | Crew jetted the line and restored flow. | Hamden | 85 Ford St, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-03-07 | 03:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Line was blocked with grease. The line was jetted and flow restored. | Hamden DPW called it in. | Less than 50 gallons. | Field estimate by crew. | No | N/A | 2023-03-07 | 03:15 PM | Crew estimated less than 50 gallons. | 40 |  | Crew jetted the line and restored flow. The area was washed down, and the catch basins were cleaned. | Hamden | 165 Howard Dr, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-03-09 | 10:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage in the city main caused the backup. | Homeowner called it in. | Less than 25 gallons. | Sewage collected in a pit the homes clean out was in. | No | N/A | 2023-03-09 | 11:15 PM | Less than 25 gallons. | 20 |  | Crew jetted the city line and restored flow. Pro Klean was contracted to clean and sanitize. | Hamden | 14 Maryknoll Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-03-09 | 12:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Roots | Tree roots were removed from the sanitary sewer. The line was cleared and flow restored.After cleani | Contractor called it in. | Less than 10 gallons. | Approximately 5 gallons of sewage was pooling in a hole next to the driveway. When the crew arrived | No | N/A | 2023-03-09 | 01:00 PM | Less than 10 gallons | 5 |  | The crew jetted the line and restored flow. The discharge may be out of a clean-out for the property | Hamden | 3 Bayberry Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-03-15 | 08:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Crew jetted the line and restored flow. The line was blocked with grease. | Homeowner called it in. | Less than 10 gallons. | Field estimate by crew. Water came up in a shower stall and stayed there. | No | N/A | 2023-03-15 | 09:00 PM | Less than 10 gallons. | 5 |  | Crew jetted the line and restored flow. Pro Klean was contracted to clean and sanitize. | Hamden | 361 Belden Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-05-18 | 09:00 AM | Lateral - Public | Raw Sewage | Sewage Line Break, Crack or Failure | Unknown at this time. Determined after excavation that private force main lateral was was cracked an | Called in by Resident Investigated by Leak Detection Service | 50 Gallons | Field Estimate | No | N/A | 2023-05-19 | 09:15 AM | Unknown | 50 |  | Excavation Scheduled for Morning of 5/19/2023 Completed and repaired by GNHWPCA Contractor | Hamden | 24 Valerie Ct, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-06-17 | 01:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Called in by homeowner | 4500 gallons | length of basement X Width of basement X depth of water X gallons per cubic foot | No |  | 2023-06-17 | 02:15 PM | 4500 Gallons (there was approx. 6in of water in basement at time of back up, clean out cap to be rem | 4500 |  | Crew jetted sewer line and restored flow. | Hamden | 25 Arcadia Ave, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-07-19 | 07:00 PM | Manhole | Raw Sewage | Unknown | Crew working to determine the cause of the by pass. | Resident called it in. | Crew estimated 3000-4000 gallons. | Field estimate by crew. | Yes | Run off from Hepburn and Corbin Rd. Water drains to State St / Quinnipiac marsh area. | 2023-07-19 | 08:30 PM | 3000-4000 gallons. | 3500 |  | Crew jetted the line. | Hamden | 70 Corbin Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-09-03 | 04:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Line partially blocked with grease. Line may be holding grease. Crew will investigate 9/5 with a CCT | Homeowner called it in. | Less than 10 gallons were discharged into the basement. | Field estimate by crew. | No | N/A | 2023-09-03 | 04:45 PM | Less than 10 gallons | 5 |  | Crew jetted the line to remove grease and restore flow. | Hamden | 161 Knob Hill Dr, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-10-10 | 02:45 PM | Manhole | Raw Sewage | Unknown | Unknown | Reported through See Click Fix. | Less than 50 gallons was discharged to the road surface. | Field estimate by crew. | No | N/A | 2023-10-10 | 03:30 PM | Less than 50 gallons. | 40 |  | Crew jetted the line and restored flow. | Hamden | 110 Stanley Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-11-09 | 08:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | A piece of broken plastic pipe was blocking the invert of the manhole. | Reported by the Regional Water Authority. | Less than 300 gallons. | Field estimate by crew. | No | N/A | 2023-11-09 | 09:30 AM | Less than 300 gallons. | 250 |  | Crew jetted the line and restored flow. The piece of pipe was removed. The crew washed the road surf | Hamden | Mix Ave, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-11-12 | 08:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage of the sanitary sewer. crew jetted the line to restore flow. Pro Klean was contracte | Homeowner called it in. | Less than 300 gallons were discharged to the basement. The sewage came up through a basement shower. | Field estimate by crew. | No | N/A | 2023-11-12 | 09:15 PM | Less than 300 gallons. | 250 |  | Crew jetted the line to restore flow. Pro Klean was contracted to clean and sanitize. | Hamden | 60 Hillcrest Ave, Hamden, CT
11356
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-01-01 | 00:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2023-01-01 | 00:30 AM | 0.0004MG | 400 |  | reduced flows | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-01-03 | 12:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2023-01-03 | 02:30 PM | 0.6266 MG | 626600 |  | reduced flows | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2023-01-12 | 07:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-12 | 11:00 PM | 3.6156 MG | 3615600 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-19 | 03:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-19 | 11:45 PM' | 2.5186 MG | 2518600 |  | end reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2023-01-20 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-20 | 01:30 AM | 1.8062 MG | 1806200 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-22 | 08:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-22 | 11:45 PM' | 1.1090 MG | 1109000 |  | end reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-01-23 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-23 | 06:15 AM | 3.7014 MG | 3701400 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-25 | 08:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-25 | 00:00 AM | 4.2867 MG | 4286700 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-26 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-27 | 00:00 AM | 12.528 MG | 12528000 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-01-27 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-01-27 | 00:15 AM | 0.0087 MG | 87000 |  | flows reduced through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-03-04 | 02:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-03-04 | 08:30 AM | 6.2839 MG | 6283900 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-03-13 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-03-14 | 00:00 AM | 1.9197 MG | 1919700 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-03-14 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-03-15 | 00:00 AM | 12.808 MG | 12808000 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-03-25 | 03:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2023-03-25 | 04:00 PM | 0.4756 MG | 475600 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-03-27 | 09:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-03-27 | 10:30 PM | 0.2071 MG | 207100 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-04-22 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2023-04-22 | 11:45 PM' | 0.1807 MG | 180700 |  | reduced flow through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-04-23 | 02:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ongoing | NA | Yes | New Haven HArbor | 2023-04-23 | 04:00 PM | 17.309 MG | 17309000 |  | reduced flow through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-04-27 | 11:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2023-04-27 | 12:00 PM | 0.2637 MG | 263700 |  | reduced flow through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-04-29 | 09:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor. | 2023-04-29 | 08:30 PM | 10.714 MG | 10714000 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-04-30 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-05-01 | 00:00 AM | 5.2315 MG | 5231500 |  | reduced flow through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-05-01 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-05-01 | 02:00 AM | 2.3867 MG | 2386700 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-05-08 | 01:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-05-08 | 02:30 AM | 0.2697 MG | 269700 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-05-20 | 12:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2023-05-21 | 00:00 AM | 17.422 MG | 17422000 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-05-21 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-05-21 | 00:30 AM | 0.0569 MG | 56900 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-06-12 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-06-13 | 00:00 AM | 0.6487 MG | 648700 |  | end of reporting day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-06-13 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-06-13 | 00:15 AM | 0.0106 MG | 10600 |  | reduced flows | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-06-14 | 05:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor | 2023-06-14 | 06:15 PM | 0.1412 MG | 141200 |  | reduced flows | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-06-27 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-06-27 | 02:45 AM | 1.9979 MG | 1997900 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-06-29 | 01:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-06-29 | 02:30 AM | 0.8192 MG | 819200 |  | rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-02 | 09:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGING | ONGING | Yes | NEW HAVEN HARBOR | 2023-07-02 | 10:30AM | 0.2624 MG | 262400 |  | rain ended/reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-03 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-07-03 | 11:45 PM' | 1.2332 MG | 1233200 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-07-04 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-07-04 | 06:15 PM | 7.9705 MG | 7970500 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-07-10 | 04:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-07-10 | 08:00 AM | 4.5866 MG | 4586600 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-16 | 10:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-07-16 | 11:15 PM | 7.9716 MG | 7971600 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-21 | 08:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | rain event | SCADA | SCADA | SCADA | Yes | NEW HARBOR | 2023-07-21 | 08:30 PM | 2.7298 MGD | 2729800 |  | NA | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-07-25 | 06:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | scada | ongoing | ongoing | Yes | New Haven harbor | 2023-07-25 | 07:45 PM | 1.6803 MGD | 1680300 |  |  | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-08-07 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-08-07 | 05:15 PM | 4.4774 MGD | 4477400 |  | Rain Event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-08-08 | 08:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-08-08 | 10:45 AM | 0.1043MGD | 104300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-08-12 | 03:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | Ongoing | Ongoing | Yes | New Haven Harbor. | 2023-08-12 | 11:45 PM' | 2.7MGD | 2700000 |  | event ended | New Haven | New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-08-13 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | rain event | SCADA | ongoing | ongoing | Yes | New Haven Harbor | 2023-08-13 | 06:30 AM | 2.4 Mgd | 2400000 |  | rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-08-15 | 04:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-08-15 | 07:00 AM | 3.2 MGD | 3200000 |  | event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-08-18 | 07:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-08-18 | 09:30 AM | 3.7 MGD | 3700000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-10 | 01:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-09-10 | 04:45 PM | 6.0644 min | 6064400 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-11 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-09-11 | 09:45 PM | 3.8981 MG | 3898100 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-13 | 04:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-09-13 | 07:00 PM | 3.4376 MG | 3437800 |  | reduced flow through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-18 | 01:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-09-18 | 11:15 PM | 2.9438 | 2943800 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-25 | 10:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-09-25 | 04:30 PM | 4.7452 MG | 4745200 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-09-29 | 04:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-09-29 | 11:30 PM | 9.1509 MG | 9150900 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-09-30 | 07:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-09-30 | 10:00 AM | 2.7769 MG | 2776900 |  | reduced flows through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-10-20 | 02:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-10-20 | 06:45 PM | 6.3040 MG | 6304000 |  | reduced flows through facility | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-10-21 | 01:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | scada | ongoing | ongoing | Yes | New Haven Harbor | 2023-10-21 | 10:00 AM | 4.9962 MG | 4996200 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-10-29 | 12:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONINGOING | ONGOING | Yes | NEWHAVEN HARBOR | 2023-10-29 | 03:00 PM | 1.7829 MG | 1782900 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-10-30 | 07:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-10-30 | 09:45 AM | 1.8488 MG | 1848800 |  | reduced flow through WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-11-22 | 03:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 12.2 MGD | ONGOING | Yes | NEW HAVEN HARBOR | 2023-11-22 | 01:00 PM | 12.2 MGD | 12200000 |  | Rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-11-26 | 11:45 PM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 0.0001 Mgd | SCADA | Yes | NEW HAVEN HARBOR | 2023-11-27 | 00:00 AM | 0.0001 Mgd | 100 |  | End of day event | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-11-27 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 1.0787 MGD | SCADA | Yes | NEW HAVEN HARBOR | 2023-11-27 | 02:00 AM | 1.0787 MGD | 1078700 |  | rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-12-01 | 08:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | SCADA | Yes | NEW HAVEN HARBOR | 2023-12-01 | 09:30 PM | 0.2976 MGD | 297600 |  | Rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-03 | 04:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | SCADA | Yes | NEW HAVEN HARBOR | 2023-12-03 | 04:30 PM | 0.1277 MGD | 127700 |  | Rain eneded | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-10 | 01:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 15.189 MGD | SCADA | Yes | NEWHAVEN HARBOR | 2023-12-11 | 00:00 AM | 15.189 MGD | 15189000 |  |  | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 2-3" per hour | 2023-12-11 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | SCADA | Yes | NEW HAVEN HARBOR | 2023-12-12 | 00:00 AM | 21.910 MGD | 21910000 |  | Rain continued to next day | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-12 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | SCADA | SCADA | Yes | NEW HAVEN HARBOR | 2023-12-12 | 00:15 AM | 0.0287 MGD | 28700 |  | event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain 1-2" per hour | 2023-12-17 | 05:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-12-17 | 09:00 AM | 3.8844 MGD | 3884400 |  |  | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-12-18 | 02:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-12-18 | 11:30 PM | 25.068 MGD | 25068000 |  | Rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-12-19 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-12-19 |  | 1.2279 MGD | 1227900 |  | Rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-12-28 | 03:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 13.083 MGD | SCADA | Yes | NEW HAVEN HARBOR | 2023-12-28 | 04:00 PM | 13.083 MGD | 13083000 |  | Rain ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-05-28 | 10:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by property owner | 1870 gallons | size of basement area X depth of water | No |  | 2023-05-28 | 11:30 PM | 1870gal (most of the water in basement initially observed drained back into system after flow was re | 1870 |  | sewer main was jetted and flow was restored by the road crew. | New Haven | 90 Concord St, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-08-17 | 08:15 AM | Treatment Plant | Partially Treated Raw Sewage | Other | Break in the Plant water line | operator tour | <5000 gallons | visually | No |  | 2023-08-17 | 08:30 AM | <5000 gallons | 3500 |  | plant water line valved out, repairs have been scheduled | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2023-12-11 | 03:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Due to heavy rain event the system is flowing at capacity. Flows at pump stations and plant are stil | Resident called it in. | Less than 100 gallons of sewage and rain water. Water is coming from the pick hole in the Manhole co | The system is still high. As the flow comes down it will stop. Bypass stopped at 4:45 PM. | Yes | Quinnipiac River | 2023-12-11 | 04:45 PM | This is still going as of 3:45 PM. Bypass ended at 4:45 PM. Less than 150 gallons were discharged to | 100 |  | Incident is ongoing until flows subside. Bypass ended at 4:45 PM. | New Haven | Quinnipiac Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-12-17 | 09:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and wipes were removed from the lateral of the fire house. The city line at the location of t | Fire Dept. called it in. | Less than 300 gallons. | Field estimate by crew. | No |  | 2023-12-17 | 09:45 PM | Less than 300 gallons. Spill was in the vehicle garage floor. | 250 |  | Crew cleaned the grease from the manhole and sanitary sewer line. Pro Klean was contracted to clean | New Haven | 125 Goffe St, New Haven, CT
294491520
[17 empty] | TOTAL VOLUME | 294503064
Report submitted with no actual release - Not counted
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-07-14 | 05:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-07-14 |  | 0Flow over 60 but time required in PID loop wasnt reached and gates did not open | 0 |  | n/a | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-10-07 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | no release | SCADA monitoring | No | NEW HAVEN HARBOR | 2023-10-07 | 06:00 PM | 0.0 mgd no release | 0 |  | no release | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | NPDES Permitted Bypass of Secondary Treatment | Rain less than 1" per hour | 2023-03-15 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | NEW HAVEN HARBOR | 2023-03-15 | 00:00 AM | 0.0 MG | 0 |  | reduced flows through the WWTF | New Haven | 345 E Shore Pkwy, New Haven, CT

## GREENWICH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 11:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Over 5.5 inches of rain from Tropical Storm Ophelia | During routine inspections of the collection system by field staff | Unknown | N/A | No | Byram River | 2023-09-30 | 04:00 PM | Unknown | 3000 |  | River went down as tide went out and rain stopped, so pumping station in area (Sout Water Street) wa | Greenwich | 163 Hervey St, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 12:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Excessive flows from Storm Ophelia - over 5.5 inches of rain recorded | Routine inspections of collection system by field staff | Unknown | N/A | No | Not sure, but believe it is Greenwich Cove | 2023-09-30 | 02:00 AM | Unknown | 3000 |  | Tides went out, rain stopped and pump station in area (Ballwood Road) was able to catch up and resum | Greenwich | 110 Shore Rd, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 12:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Excessive flows from storm event - Ophelia - over 5.5 inches of rain recorded | Visually observed by field staff performing inspections of the collection system | Unknown | N/A | No | Not completely sure, but believe it is Greenwich Cove | 2023-09-30 | 00:00 AM | Unknown | 3000 |  | Tide went out, rain stopped and pump station in area (Station A) was able to catch up and resume nor | Greenwich | 17 Roosevelt Ave, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 11:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Over 5.5 inches of rain from Tropical Storm Ophelia | During routine inspections of sanitary sewer system by field staff | Unknown | N/A | Yes | Byram River | 2023-09-30 | 07:30 AM | Unknown | 3000 |  | River went down as tide went out, rain stopped and pump station in area (Ballwood Road) was able to | Greenwich | 16 N Water St, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 11:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Significant rainfall from Storm Ophelia - over 5.5 inches of rain | During routine inspections by our field staff of the collection system | Unknown at this time | Not Applicable | Yes | Byram River | 2023-09-30 | 11:00 AM | Unknown | 3000 |  | River went down when tide went out, rain stopped and pump station in area (South Water Street) was a | Greenwich | 59 S Water St, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 11:30 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Excessive flows from Storm Ophelia | Visually by plant process control manager checking the tanks, etc. | Unknown | Unknown | Yes | Greenwich Harbor | 2023-09-30 | 00:00 AM | 20,000 gallons of primary effluent overtopped the distribution channel of the aeration system but di | 20000 |  | The incident resolved after the rain slowed and the tide went out. The plant pumping equipment was a | Greenwich | Grass Island Rd, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2023-03-29 | 03:30 PM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility |  | Phone call report of water coming out around utility pole from local water company (Aquarion Water) | Unknown at time of event | Undetermined at time of event | Yes | A portion of the wastewater that came to the surface ran over the grass, then over the curb and into | 2023-03-29 | 08:00 PM | Estimated at 2 gpm with one pump running for a maximum 30 minutes per hour x 4.5 hours of known disc | 270 |  | We turned off the pumps at the pump station, utilized septic hauler trucks to vac out of the wet wel | Greenwich | 108 S Water St, Greenwich, CT
[17 empty] | TOTAL VOLUME | 35270

## GISWOLD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
JEWETT CITY WPCA | Closed | Sewage Bypass | Dry | 2023-12-19 | 07:00 AM | Select... | Raw Sewage | Excessive Flows - Storm Event |  | Upon operator arrival to the plant |  |  | Yes | Quinnebaug River | 12/19/2023 | 12:00 PM | 500 | 500 |  |  | Griswold | 52 Wedgewood Dr, Griswold, CT
JEWETT CITY WPCA | Closed | Sewage Bypass | Dry | 2023-11-08 | 11:00 AM | Manhole | Raw Sewage | Sewer Line Blockage - Other | unknow until line is jetted. | Resident called in sewage coming into basement. | 300-500 gallons | visual | No |  | 11/8/23 | 03:00 PM | 500 | 500 |  |  | Griswold | 15 Wilson St, Griswold, CT
JEWETT CITY WPCA | Closed | Sewage Bypass | Dry | 2023-05-13 | 09:00 PM | Pump Station | Raw Sewage | Other | The three pumps at Burleson Lane station were not keeping up with the flow in wet well. Flow was bac | Resident noted sewage discharge into River and called number on station gate. Alarm company then not | 100-300 gallons | Visual | Yes | Quinebaug River | 2023-05-14 | 00:00 AM | 100-300 gallons | 250 |  | Tested and removed Pump#3; found no clogs and clear ofdebris. Inspected the check valves and found t | Griswold | 38 Burleson Ln, Griswold, CT
[17 empty] | TOTAL VOLUME | 1250

## GROTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2023-10-05 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Visual check of manhole | 200-300 Gallons | Visual estimate, pump station flows. | Yes | Birch plain creek | 2023-10-05 | 02:30 AM | 200-300 gallons | 250 |  | Sewer jet truck cleared blockage - flow resumed immediately | Groton | 149 Madison Pl, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Dry | 2023-08-21 | 01:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Notified by Groton Utilities (water company) | unknown. very small amount | Small office park. Estimated based on length of time and reported flow rate | No |  | 2023-08-21 | 02:00 PM | Unknown | 0 |  | Private sewer jetted clear and debris physically removed | Groton | 481 Gold Star Hwy, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Dry | 2023-04-10 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Sewer force main break | Water Company responded to customer call, determined it was sewer and notified WPCD | 30 gpm | estimate flow | Yes | Enters storms collection system, drains into 1 acre of wetland, then to Haley Brook, which eventuall | 2023-04-10 | 02:00 PM | 9000 gals | 9000 |  | Septic haulers onsite at 2 pm, to bypass broken force main. Contractor onsite 2pm to repair forcema | Groton | 55 Pumpkin Hill Rd, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Dry | 2023-01-19 | 07:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Sewer line blockage. | Drew Hagerty (Beacon Point Property Manager) discovered the sewage main blockage. | >100 Gallons | Estimated based on flow rate and time. | No |  | 2023-01-19 | 09:30 AM | More than 100 gallons. | 200 |  | Blockage removed and lime placed on ground surface. No recoverable sewage in the storm system. | Groton | 26 Highland Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2023-12-12 | 11:45 AM' | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Backup near lift station. | UEM noticed sewage back up while doing work in the area. | 50 | Visual | Yes | Thames River is possibly affected but not positive if sewage reached the river after entering stormd | 2023-12-12 | 01:00 PM | 50 | 50 |  | Blockage was removed and bypass fixed. | Groton | 1 Crystal Lake Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2023-09-22 | 06:45 PM | Lateral - Public | Raw Sewage | Sewage Line Blockage - Other | Likely to be trees. | Resident complaint. | N/A for environment--~10 gallons into home. | Local estimate. | No | N/A | 2023-09-22 | 07:45 PM | 0 due to no release. All sewage remained in lateral line. | 0 |  | Lateral line replaced and no release to environment. | Groton | 55 Hornbeam Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2023-07-22 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Resident reported | <10 Gallons | On-site supervisor | No | N/A | 2023-07-22 | 03:30 PM | <10 Gallons | 10 |  | Blockage was cleared and sewer level backed down and is flowing normally again. | Groton | 11 Lake St, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2023-04-28 | 02:30 PM | Sewer Main | Raw Sewage | Unknown | Public Works was on scene with Environmental and noticed a broken toilet draining to sewer main. Wat | Noticed by public works. | 20 Gallons | Visual | No |  | 2023-04-28 | 03:00 PM | 20 Gallon | 20 |  | Pumps to sewer main shut off. No flow to broken main. | Groton | 1 Crystal Lake Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Other | 2023-04-16 | 04:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Resident reported | Unknown, Public Works Dept on site.Update: Pipefitter estimated a few gallons backed up, some of wh | N/A at this time.Update: On-site supervisor estimate. | No | N/A | 2023-04-16 | 06:30 PM | ~10 gallons | 10 |  | Jetted the line , observed normal flow return, and applied garden lime to wet surface areas. | Groton | 148 Dewey Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2023-04-14 | 11:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Small pool of water surrounding manhole, reported to Fire Dept and Public Works. | <100 gallons total, ~5 gallons may have entered a nearby Storm drain. | On-site supervisor estimate. | No |  | 2023-04-14 | 12:30 PM | <100 Gallons | 75 |  | Blocked nearby drains, used jetting tool to clear blockage, applied and recovered lime to affected a | Groton | Amberjack Rd, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Other | 2023-03-02 | 07:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | N/A | Resident report (Navy Housing) | 100 gallons | On-site supervisor estimate | No | N/A | 2023-03-02 | 08:30 AM | ~ 100 gallons | 100 |  | Cleared blockage, observed level fall and normal flow. | Groton | 54 Magnolia Dr, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2023-01-21 | 12:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Sewage backup. | Housing manager discovered backup and called Fire Department. | 100 gallons | Rate of flow and time | No |  | 2023-01-21 | 02:15 AM | More than 100 gallons. | 200 |  | Garden lime spread over spill. No standing waste water in storm sewer. | Groton | 26 Highland Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2023-01-19 | 12:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Debris in line. Line cleared | SUBASE Pipefitters found a buried manhole on the north side of B103 from which the backup surfaced. | Less than 1 gallon. | Visual. | No |  | 2023-01-19 | 01:00 PM | 1 Gallon | 1 |  | Line cleared. Release to grass. Nothing could be done. | Groton | 1 Crystal Lake Rd, Groton, CT
[17 empty] | TOTAL VOLUME | 9916

## KILLINGLY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
KILLINGLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-19 | 07:00 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | Heavy wind and rain caused trees and limbs to fall. This created power outages at the South Shore Pu | Mission communications and phone calls. | 500 from manhole, 1000 in private basements | Visual estimate | No |  | 2023-12-19 | 04:00 PM | 2000 gallons | 2000 |  | Trees and limbs were removed from power lines making is so crews could bring portable generators to | Killingly | 8 Lawton Ln, Killingly, CT
KILLINGLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 02:00 AM | Manhole | Raw Sewage | Electrical Equipment Failure | Main feed transformer is not operating. We are able to run pumps on hand, since there is no control | Mission alarm | 50 gals. Manhole started leaking as pumps were put on hand. | Visual | No |  | 2023-07-16 | 12:00 PM | 50 gallons | 50 |  | Electricity repaired | Brooklyn | 32 Tatnic Rd, Brooklyn, CT
[17 empty] | TOTAL VOLUME | 2050

## LITCHFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
LITCHFIELD WPCF | Closed | Sewage Bypass | Dry | 2023-10-24 | 09:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Excessive rocks and grit somehow entered the lateral after the grease tank. We suspect that the heav | An employee of the school noticed sewage seeping out of a manhole. | We estimated that only 20 gallons seeped onto the grass and over a sidewalk. No sewage reached a ca | Visual observations. | No |  | 2023-10-24 | 11:00 AM | 20 gallons. | 20 |  | We jetted about 60 ft. of their private lateral to break free the blockage. Litchfield High School w | Litchfield | 14 Plumb Hill Rd, Litchfield, CT
LITCHFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 01:15 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | We also had to open up the UV bypass channel to reduce the possibility of the UV tank over flowing | Operator observations. | From the diversion tank it may have only been less than 10,000 gallons. Now that the UV bypass chann | From the diversion tank it was from observing how the secondary tanks looked, and that most of the f | Yes | Bantam River. | 2023-09-30 | 07:30 AM | 2.6 MG | 2600000 |  | We closed the UV by channel and began properly disinfecting all effluent at 7:30 AM on 9/30/23. The | Litchfield | 29 Stoddard Rd, Litchfield, CT
LITCHFIELD WPCF | Closed | Sewage Bypass | Dry | 2023-06-30 | 09:00 AM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure | The cast iron pipe in the basement had a crack in it. | By the employees who work at the school. | Unknown but we would think less than 30 gallons, based on the water stain on the basement floor. | There was only summer school this morning and they called the plumber this morning when they had to | No | The sewage reached a wetlands area where this building drain emptied out, which was dry at the time. | 2023-06-30 | 10:00 AM | Undetermined but we estimated less than 30 gallons. The school had a restoration company do a prope | 25 |  | First the plumber cleared the blockage in the plumbing in the basement of the school. Second the p | Litchfield | 5 Knife Shop Rd, Litchfield, CT
[17 empty] | TOTAL VOLUME | 2600045

## MANCHESTER
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2023-04-03 | 10:00 AM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure | The ultrasonic level sensor level was not reading correctly/having issues, so the sensor was swapped | By one of the employees dewatering and doing a equipment/building walkaround. | 20 feet x 15 feet x .25 feet area of foam.75 cubic foot area if calculated out in gallons this equal | By area calculation of foam. Calculated the cubic area as if it was liquid | No |  | 2023-04-03 | 11:30 AM | 20 feet x 15 feet x .25 feet area of foam.75 cubic foot area if calculated out in gallons this equal | 561 |  | Centrifuge was slowed down and hoses used to hose down foam in wet well. Instrumentation specialist | Manchester | 120 Thrall Rd, Manchester, CT
MANCHESTER 8th DISTRICT | Closed | Sewage Bypass | Dry | 2023-02-06 | 01:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags |  | Resident at 433 North Main Street called in the overflowing manhole | UNknown - unsure when started | 100gal/min is size of main | Yes | Hockanum RIver | 2023-02-06 | 03:45 PM | 1050 gallons | 1050 |  | Using the vac/flush truck to clear the blockage and remove the debris from the line | Manchester | 433 N Main St, Manchester, CT
[17 empty] | TOTAL VOLUME | 1611

## MANSFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
UNIVERSITY OF CONNECTICUT | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-18 | 10:30AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | Scada MonitoringWet well level known on SCADA for overflow level.Physical monitoring of a dispatched | Approximately 36000- 40000 Event time was 10:15am to 12:35 Above approximation stands, no change.. | Pump/Pipe capacity 1000 gpmEstimated 250 GPM lost/2.5 hours.Flows are already subsiding will update | No |  | 2023-12-18 | 12:45 PM | Approximately 36000- 40000 Event time was 10:15am to 12:35 Above approximation stands, no change.. | 380000 | Pump/Pipe capacity 1000 gpm | Storm ended | Mansfield | 30 Plains Rd, Mansfield, CT
UNIVERSITY OF CONNECTICUT | Closed | Sewage Bypass | Dry | 2023-02-15 | 12:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | It was called in and noticed by Facilities that were in the area. | undetermined but quantity is low based on low flows. | unknown | No |  | 2023-02-15 | 04:00 AM | minimal <5000 gallon | 4000 | Estimated 250 GPM lost/2.5 hours. | Public Works repaired the pipe. | Mansfield | Mansfield, CT
[17 empty] | TOTAL VOLUME | 384000

## MDC
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-28 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home Owner | <100g | MDC personnel | No |  | 2023-12-28 | 05:00 PM | <100g | 75 |  | JET TRUCK RELIEVED STOPPAGE | Bloomfield | 11 Musket Trail, Bloomfield, CT
75
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-28 | 07:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | <1000G | MDC PERSONEL | Yes | TROUT BROOK | 2023-12-28 | 11:00 AM | 0.061mg | 61000 |  | main sewer flushed by jet truck , stoppage relieved | East Hartford | 145 Main St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-28 | 06:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | <1000G | MDC PERSONNEL | Yes | PIPER BROOK | 2023-12-29 | 11:30 PM | 19.601 MG | 19601000 |  | Levels receded | East Hartford | 59 Chester St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-12-19 | 05:00 PM | Basement | Raw Sewage | Unknown |  | Home owner | <100gls | visual observation MDC personnel | No |  | 2023-12-19 | 07:00 PM | <100gals | 75 |  | JET TRUCK RELIEVED SEWER - REPAIRS BEING MADE TODAY 1/10/2023 | East Hartford | 12 Spring St, East Hartford, CT
19662075
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 11:30 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event | Home owner | <100g | MDC personnel | No |  | 2023-12-19 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | 239 1/2 Brainard Rd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 11:15 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Bypass due to wet weather event | MDC personnel | <1000g | MDC personnel | Yes | Webster Brook | 2023-12-18 | 10:30 PM | 260,000GALS | 260000 |  | MDC repaired sewer pipe | Hartford | 50 Stonington St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-12-18 | 04:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Wet weather event | MDC SCADA | LESS THAN 1000 | MDC SCADA | Yes | TROUT BROOK | 2023-12-19 | 00:30 AM | 8.511mg | 8511000 |  | FLUSHED SEWER MAIN TO RELIEVE SLIGHT BLOCKAGE OF DEBRIS | Hartford | 461 Capitol Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 02:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | MAIN SEWER SURCHARGED DUE TO RAIN EVENT | MDC PERSONNEL | 10,000 GALLONS | MDC PERSONNEL | Yes | TROUT BROOK | 2023-12-19 | 08:00 AM | 50000 - 75000g | 70000 |  | Levels receded | Hartford | 239 1/2 Brainard Rd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-12-18 | 04:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT | MDC SCADA | 0.675mg | MDC SCADA | Yes | TROUT BROOK | 2023-12-18 | 06:30 PM | 0.675mg | 675000 |  | JET TRUCK RELIEVED MAIN SEWER | Hartford | 130 Murphy Rd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-12-18 | 03:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1,000 GALLONS | MDC SCADA | Yes | PIPER BROOK | 2023-12-20 | 05:15 PM | 18.123mg | 18123000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 43 Bolton St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 01:30 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | electrical issue with pump station | MDC personnel to make repairs | 120000gal | MDC personnel | Yes | Piper Brook | 2023-12-18 | 02:30 PM | 120000gal | 120000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 136 Maple Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 01:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | MAIN SEWER SURCHARGED DUE TO RAIN EVENT | DISCOVERED BY CITY OF HARTFORD PUBLIC WORKS | 10,000 GALLONS | MDC PERSONNEL | Yes | CONNECTICUT RIVER | 2023-12-19 | 00:00 AM | 25000-50000g | 40000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 369 Granby St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 02:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | MAIN SEWER SURCHARGED DUE TO RAIN EVENT | TOWN OF WEST HARTFORD PUBLIC WORKS | 1000-10000g | MDC PERSONNEL | Yes | Trout Brook | 2023-12-19 | 08:00 AM | 10000g-50000g | 40000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 693 Garden St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 03:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Surcharge due to wet weather event | Home owner | <100g | MDC personnel | No |  | 2023-12-19 | 08:00 AM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 12 Amherst St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 01:00 PM | Lateral - Private | Raw Sewage | Excessive Flows - Storm Event | Main sewer surcharged due to Rain event | MDC personnel | <100 | MDC personnel | No |  | 2023-12-19 | 08:00 AM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 77 Goodrich St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-12-18 | 05:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Newington Police Department | <100mg | observation MDC personnel | Yes | Mill Brook | 2023-12-19 | 08:00 AM | 1000-25000g | 20000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 82 Ward St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-11 | 02:00 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | MDC personnel | 192,000g | MDC Personnel | Yes | Webster Brook | 2023-12-11 | 10:30AM | 192,000 | 192000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 31 Webster St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-11 | 00:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT | MDC SCADA SYSTEM | <1000GALLONS | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2023-12-11 | 06:00 AM | 36,000g | 36000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 65 Harwich St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-10 | 10:30 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | 0.278MG | NDC SCADA | Yes | PIPER BROOK | 2023-12-12 | 12:00 PM | 10.155MG | 10155000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 373 Granby St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-10 | 10:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT | MDC SCADA SYSTEM | 0.321MG | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2023-12-11 | 10:30AM | 3.857mg | 3857000 |  | Bypass is eliminated once flows drop to normal flows. | Hartford | 950 Tower Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-11-15 | 11:45 AM' | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | Yes | MILL BROOK | 2023-11-15 | 12:30 PM | TOTAL GALLONS = 500 GALLONS | 500 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 127 South St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-11-01 | 01:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Collapse pipe | MDC PERSONAL | <100 GALLONS | MDC PERSONAL | Yes | Folly Brook | 2023-11-01 | 07:00 PM | 100-1000 gallons | 750 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 920 Maple Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-10-16 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | SLIGHT BLOCKAGE DUE TO BUILD UP OF TWIGS | SCADA | > 1,000 GALLONS | SCADA | Yes | PARK RIVER CONDUIT | 2023-10-16 | 10:00 AM | TOTAL GALLONS = 200 GALLONS | 200 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | Airport Rd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-10-07 | 10:15 PM | Basement | Raw Sewage | Unknown |  | Homeowner | <100G | MDC Personnel | No |  | 2023-10-08 | 00:00 AM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 70 Plymouth St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-10-05 | 08:15 PM | Basement | Raw Sewage | Unknown |  | Homeowner | <100g | MDC PERSONNEL | No |  | 2023-10-05 | 09:30 PM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 16 Lorraine St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-10-04 | 05:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | HOME OWNER | <100gals | visual observation MDC personnel | No |  | 2023-10-04 | 07:30 PM | <100gals | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Hartford | 336 Franklin Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 10:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <11000g | MDC personnel | Yes | North Branch | 2023-09-30 | 06:00 PM | 100-1000g | 750 |  | Sewer main repaired | Hartford | 448 Prospect Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 01:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | HOMEOWNER | <100gals | VISUAL OBSERVATION | No |  | 2023-09-30 | 02:00 PM | <100g | 75 |  | Repair made to damaged sewer main. | Hartford | 1078 Capitol Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 04:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | REPAIRED DEMAGED SEWER MAIN | Hartford | 142 Nilan St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-30 | 00:30 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Per homeowner | <100 gals | Per MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Rain event - levels have receded | Hartford | 30 Airport Rd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 12:45 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | Broad St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 10:15 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100gals | visual observation | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Rain event - levels have receded | Hartford | 7 Kane St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 02:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <1000g | MDC personnel | Yes | Bass Brook | 2023-10-01 | 08:00 AM | 1000-25000g | 20000 |  | Rain event - levels have receded | Hartford | 188 Sigourney St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Other | 2023-09-30 | 09:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Rain event - levels have receded | Hartford | 80 Charter Oak Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 07:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  |  | <1000gals | visual observation | Yes | GOFF BROOK | 2023-10-01 | 08:00 AM | 1000-25000g | 20000 |  | Levels receded | Hartford | 10 Wilbur St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-30 | 09:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Call from Windsor P.D. | <100 gals | Visual Observation | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | 74 Harwich St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-30 | 08:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | <100 GALS | VISUAL INSPECTION | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | Locust St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 09:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC personnel | <1000g | MDC personnel | Yes | Folly Brook | 2023-10-01 | 08:00 AM | 1000-25000 | 20000 |  | Levels receded | Hartford | 77 Goodrich St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 09:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDCpersonnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | 383 Granby St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | 373 Granby St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 06:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | 9 Wilbur St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 09:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Levels receded | Hartford | 31 Webster St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 08:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | ALL LEVEL RECEDED | Hartford | 1205 Albany Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-09-30 | 03:00 PM | <100g | 75 |  | Surcharge levels receded | Hartford | 110 Standish St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 10:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | ALL LEVEL RECEDED | Hartford | 23 Bulkeley Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 08:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | <1000 GALS | VISUAL OBSERVATION | Yes | TROUT BROOK | 2023-10-01 | 01:45 PM | 20.406mg | 20406000 |  | Weather event has ended - levels receded | Hartford | 127 South St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <1000g | MDC personnel | No |  | 2023-10-02 | 12:00 PM | 100-500g | 450 |  | ALL LEVEL RECEDED | Hartford | 711 Garden St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 12:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-09-30 | 12:00 PM | <100g | 75 |  | ALL LEVEL RECEDED | Hartford | 69-71 Cabot St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 10:30AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | WINDSOR PD | <1000 | VISUAL OBSERVATION | Yes | DECKERS BROOK | 2023-10-01 | 08:00 AM | 75000 - 10000g | 90000 |  | Surcharge levels receded | Hartford | 24 Bannister St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 10:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | HOME OWNER | < 100gals | mdc personnel | No |  | 2023-09-29 | 11:30 AM | <100 gals | 75 |  | ALL LEVEL RECEDED | Hartford | 670 Hillside Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 09:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Wet weather surcharge - levels receded | Hartford | 18 Kelsey St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 09:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC Scada system | <1000gals | visual observation | Yes | Trout Brook | 2023-09-30 | 12:45 PM | 0.694mg | 694000 |  | Weather event has ended | Hartford | 127 Gilman St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 01:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Passerby | <1000g | MDC personnel | Yes | Trout Brook | 2023-10-01 | 08:00 AM | 25000 - 50000g | 40000 |  | Rain event - levels have receded | Hartford | 80 Charter Oak Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-09-30 | 12:30 PM | <100g | 75 |  | ONCE ELEVATED SEWER FLOWS RECEDE BACK TO NORMAL. | Hartford | 924 Wethersfield Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC personnel | <1000g | MDC personnel | Yes | Trout Brook | 2023-10-01 | 08:00 AM | 100,000 - 500,000g | 450000 |  | Once elevated sewer flows recede back to normal. | Hartford | 14 Arlington St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 09:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC personnel | <1000 | MDC personnel | Yes | Folly Brook | 2023-10-01 | 08:00 AM | 1000-25000g | 20000 |  | Once elevated sewer flows recede back to normal. | Hartford | 451 Cornwall St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 06:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-10-01 | 08:00 AM | <100g | 75 |  | Once elevated sewer flow receded back to normal. | Hartford | 450 Granby St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 01:45 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | MDC personnel | Unknown | Unknown | Yes | Webster Brook | 2023-09-30 | 05:30 PM | 454,000gal | 454000 |  | ONCE ELEVATED SEWER FLOW RECEDE BACK TO NORMAL. | Hartford | 80 Charter Oak Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-09-30 | 01:30 PM | <100g | 75 |  | Jet ruck relieved M/S | Hartford | Enfield St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Town of West Hartford | <1000g | MDC personnel | Yes | Trout Brook | 2023-10-01 | 08:00 AM | 25000 - 50000g | 40000 |  | M/S to be repaired - Bypass pumping M/S | Hartford | 2309 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 04:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC Personnel | No |  | 2023-09-26 | 02:00 AM | <100g | 75 |  | Repairs continue - Final report to follow | Hartford | 2345 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 11:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC personnel | 1000g | MDC personnel | Yes | Beaver Brook | 2023-09-26 | 02:00 AM | 1000-25000g | 20000 |  | Repairs to MDC M/S - bypass pumping | Hartford | 2319 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 09:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Wet weather event | MDC personnel | <1000g | MDC personnel | No |  | 2023-09-26 | 03:00 AM | 25000-50000g | 40000 |  | Bypass pumping - SSO has endedRepairs to M/S being performed | Hartford | 2327 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 09:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Resident | 1000-10000g | MDC Personnel | Yes | Park River | 2023-09-26 | 00:00 AM | 1000-25000g | 20000 |  | Repairs made to main sewer | Hartford | Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-26 | 01:00 AM | <100g | 75 |  | Repairs continue - Final report to follow | Hartford | 2335 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 06:45 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | SCADA | > 100 | MDC PERSONNEL | No |  | 2023-09-26 | 03:00 AM | 523,200gal | 523200 |  | MDC REPAIRED SEWERBY-PASS HAS ENDED - REPAIRS COMPLETED | Hartford | Farmington Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-25 | 11:00 PM | <100g | 75 |  | MDC RELIEVED STOPPAGE BY JET TRUCK | Hartford | Farmington Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 09:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Wet weather event | Resident | <100g | Visual | Yes | Trout Brook | 2023-09-26 | 02:00 AM | 1000-25000g | 20000 |  | JET TRUCK RELIEVED SEWER - DEBRIS | Hartford | 298 Barbour St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 09:30 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-25 | 10:00 PM | <100g | 75 |  | REPAIRS MADE TO M/S | Hartford | 95 Vine St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 12:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-25 | 11:00 PM | <100g | 75 |  | MDC CREWS MADE EMERGENCY REPAIRS | Hartford | 114 Vine St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 10:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-25 | 10:00 PM | <100g | 75 |  | MDC CREWS FIXED DAMAGED PIPE | Hartford | 107 Vine St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 03:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Bye MDC Scada System | <1000gals | bye MDC Scada System | Yes | Trout Brook | 2023-09-26 | 02:15 PM | 10.806 | 10806000 |  | MDC crews repaired Main Sewer | Hartford | 95 Vine St, Hartford, CT
HARTFORD WPCF (MDC) | Closed | Sewage Bypass | Rain greater than 4" per hour | 2023-07-21 | 04:45 PM | Treatment Plant | Raw Sewage | Electrical Equipment Failure | supply power from Eversource was lost for a short period causing the influent pumps to stop pumping. | Plant operations personnel drove the plant roadways and noticed the roadways had sewage on them. | < 5000 gallons | length of non pumping / wet well level. | No |  | 2023-07-21 | 05:00 PM | < 5000 gallons | 4000 |  |  | Hartford | 240 Brainard Rd, Hartford, CT
75791325
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 09:30 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC Personnel | No |  | 2023-09-25 | 10:00 PM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back tonormal | Newington | 109 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC Personnel | No |  | 2023-09-25 | 11:00 PM | <100g | 75 |  | Issues corrected - Final report | Newington | 103 Brookside Rd, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 10:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-25 | 10:00 PM | <100g | 75 |  | Levels receded | Newington | 175 Cedar St, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-25 | 11:00 PM | <100g | 75 |  | Levels receeded | Newington | 109 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 03:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | PER SCADA SYSTEM | <1000gals | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2023-10-03 | 02:30 PM | TOTAL GALLONS: 60.131 MG | 60131000 |  | Main sewer flushed by jet truck and stoppage relieved. | Newington | 40 Welles Dr N, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home Owner | <100g | MDC personnel | No |  | 2023-09-25 | 10:00 PM | <100g | 75 |  | Levels receded | Newington | 61 Groveland Terrace, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 10:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Resident | 1000 - 25000g | MDC personnel | Yes | Beaver Brook | 2023-09-26 | 02:00 AM | 1000-25000g | 20000 |  | Levels receded | Newington | 87 Chestnut Rd, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 05:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | EVENT IS ONGOING | PER MDC SCADA | <1000gals | PER MDC SCADA SYSTEM | Yes | TROUT BROOK DR | 2023-09-25 | 11:00 PM | 0.615mg | 615000 |  | Levels receded | Newington | 114 Chestnut Rd, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 11:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC personnel | 1000g | MDC personnel | Yes | Beaver Brook | 2023-09-26 | 02:00 AM | 1000-25000g | 20000 |  | Levels receded | Newington | 56 Chestnut Rd, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 01:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC personnel | No |  | 2023-09-25 | 11:00 PM | <100g | 75 |  | Levels receded | Newington | 187 Stonehedge Dr, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 12:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Resident | 1000g | MDC personnel | Yes | Rockhole Brook | 2023-09-26 | 09:30 AM | 25000-50000g | 40000 |  | Main Sewer flushed w/jet truck | Newington | 172 Indian Hill Rd, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 09:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | <1000GALS | Visual observation | Yes | Trout Brook | 2023-09-26 | 07:00 AM | 25000-50000g | 40000 |  | Levels receded | Newington | 614 Maple Hill Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-09-20 | 10:30AM | Manhole | Raw Sewage | Unknown | Debris | town of WH public works | <10gallons | MDC Personnel | No |  | 2023-09-20 | 11:30 AM | <5g - small puddle | 5 |  | Levels receded | Newington | 109 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-18 | 09:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | .080MG | SCADA SYSTEM | Yes | PIPER BROOK | 2023-09-19 | 01:30 PM | 2.833MG | 2833000 |  | Levels receded | Newington | 574 Maple Hill Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-18 | 10:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT | MDC SCADA | .201MG | MDC SCADA | Yes | TROUT BROOK | 2023-09-19 | 01:15 AM | 0.471mg | 471000 |  | Levels receded | Newington | 898 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-09-15 | 03:00 PM | Manhole | Raw Sewage | Unknown |  | MDC PERSONNEL | <100G | MDC PERSONNEL | No |  | 2023-09-15 | 03:30 PM | <100G | 75 |  | Levels receded | Newington | 19 Brook St, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receded | Newington | 357 Main St, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receded | Newington | 283 Tremont St, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 05:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - M/S Surcharged | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receded | Newington | 29 Occhialini Ct, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - M/S Surcharged | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | WET WEATHER EVENT ENDED EXTRANEOUS FLOWS SUBSIDED | Newington | 109 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | RAIN EVENT ENDED EXTRANEOUS FLOWS SUBSIDED | Newington | 111 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Surcharge of M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | > 100 | 75 |  | Main line sewer flushed by Jet truck | Newington | 300 Alumni Rd, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 110 |  | MDC jet truck relieved stoppage - Event has ended | Newington | 59 Wilbur Dr, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Rain event ended - flows receded | Newington | 111 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-09-13 | 10:30AM | Basement | Raw Sewage | Excessive Flows - Storm Event | MAIN SEWER SURCHARGED DUE TO RAIN EVENT | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No |  | 2023-09-13 | 10:00 PM | < 100 | 75 |  | SURCHARGE LEVELS RECEEDED | Newington | 109 Carr Ave, Newington, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - M/S Surcharged | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Main Sewer flushed by Jet Truck, blockage relieved | Newington | 331 Tremont St, Newington, CT
64171315
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receded | West Hartford | Quaker Ln S, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | EVENT HAS ENDED | West Hartford | 83 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 12:00 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | MDC Personnel | <100g p/hr | MDC Personnel | Yes | Webster Brook | 2023-09-13 | 11:45 PM' | 200,000 +/- | 200000 |  | Main sewer flushed by jet truck, stoppage relieved | West Hartford | 55 Grove St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - M/S Surcharged | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receeded | West Hartford | 29 Hall St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receeded | West Hartford | Chelton Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 10:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | FLASH FLOODING DUE TO RAIN EVENT | SCADA | > 100,000 GALLONS | SCADA | Yes | TROUT BROOK | 2023-09-13 | 07:00 PM | 2.69 MG | 2690000 |  | Levels receded | West Hartford | 1 Fox Meadow Ln, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receeded | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 10:15 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | FLASH FLOODING DUE TO RAIN EVENT | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No |  | 2023-09-13 | 10:00 PM | < 100 | 75 |  | Levels receded | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 11:15 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | MAIN SEWER SURCHARGED DUE TO RAIN EVENT | MDC PERSONNEL | < 100 | MDC PERSONNEL | No |  | 2023-09-13 | 10:00 PM | < 100 | 75 |  | Levels receded | West Hartford | 11 Wyndwood Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 10:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | FLASH FLOODING DUE TO RAIN EVENT | SCADA | > 100,000 GALLONS | SCADA | Yes | PIPER BROOK | 2023-09-14 | 10:45 PM | 9.128mg | 9128000 |  | Levels receded | West Hartford | 25 Linbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | LEVELS RECEEDED | West Hartford | 200 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 10:15 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | FLASH FLOODING DUE TO RAIN EVENT | MDC PERSONNEL | < 100,000 GALLONS | MDC PERSONNEL | No |  | 2023-09-13 | 12:30 PM | < 1000 Gallons | 750 |  | Bypass is eliminated once flows drop below overflow | West Hartford | 85 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 01:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | LEVELS RECEEDED | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 01:00 PM | Select... | Raw Sewage | Excessive Flows - Storm Event | Wet weather event - Surcharged M/S | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Main Sewer Relieved by Jet Truck | West Hartford | 36 Westfield Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - M/S Surcharged | Home Owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Main sewer relieved by Jet Truck | West Hartford | 17 Mozart St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-13 | 02:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Wet Weather Event - M/S Surcharged | Home owner | <100g | MDC personnel | No |  | 2023-09-13 | 10:00 PM | <100 | 75 |  | Levels receded | West Hartford | 200 Bloomfield Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-13 | 10:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | FLASH FLOODING DUE TO RAIN EVENT | SCADA | > 100,000 GALLONS | SCADA | Yes | TROUT BROOK | 2023-09-13 | 12:45 PM | 543,000 Gallons | 543000 |  | Jet ruck relieved M/S - Event has ended | West Hartford | 24 Grove St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-09 | 08:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT | MDC SCADA SYSTEM | 0.001MG | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2023-09-10 | 05:30 AM | 1.454mg | 1454000 |  | Levels receded | West Hartford | 186 Newington Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-09 | 09:15 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | >100,000MG | MDC PERSONNEL | Yes | WEBSTER BROOK | 2023-09-10 | 02:45 AM | 20,000 GAL | 20000 |  | Levels receded | West Hartford | 75 Hall St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-09-04 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Reported by Police Department | <100 gals | MDC employee | Yes | Piper Brook | 2023-09-04 | 01:30 PM | <100 gls | 75 |  | Levels receded | West Hartford | 32 Brian Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-08-22 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease | Resident / town reported | <100g | MDC personnel | Yes | Mill Brook | 2023-08-22 | 01:45 PM | <100g | 75 |  | Levels receded | West Hartford | 121 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-08-18 | 08:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA System | 0.208mg | MDC SCADA System | Yes | Piper Brook | 2023-08-18 | 02:15 PM | 0.877mg | 877000 |  | Levels receded | West Hartford | 200 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-08-01 | 04:15 PM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure |  | Home owner report | <100gals | MDC personel | No |  | 2023-08-01 | 06:00 PM | <100 gallons | 75 |  | Levels receded | West Hartford | 69 Linbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-08-01 | 05:45 PM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure |  | MDC personnel | TBD | MDC personnel | No |  | 2023-08-01 | 09:30 PM | 135000 Gallons | 135000 |  | Levels receded | West Hartford | 1 Fox Meadow Ln, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-08-01 | 05:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Contractor / Plumber | <100gals | mdc personnel | No |  | 2023-08-08 | 06:45 PM | 20gals | 20 |  | Levels receded | West Hartford | 11 Wyndwood Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-07-31 | 02:15 PM | Select... | Raw Sewage | Sewage Line Break, Crack or Failure |  | MDC PERSONNEL | TBD | MDC PERSONNEL | No |  | 2023-08-01 | 02:30 AM | 30,000 Gallons | 30000 |  | Level receded | West Hartford | 4 Overbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-07-29 | 03:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | FIRE DEPARTMENT | <100G | MDC PERSONNEL | No |  | 2023-07-29 | 04:30 PM | <100g | 75 |  | Levels receded | West Hartford | 35 Ringgold St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-07-29 | 04:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | <100G | MDC PERSONNEL | Yes | CT RIVER | 2023-07-29 | 05:00 PM | <100G | 75 |  | Duplicate Report - Please disregard | West Hartford | 6 Wyndwood Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-07-29 | 03:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | FIRE DEPARTMENT | <100G | MDC PERSONNEL | No |  | 2023-07-29 | 05:00 PM | <100g | 75 |  | Levels receded | West Hartford | N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-07-29 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOMEOWNER | <100G | MDC PERSONEL | No |  | 2023-07-29 | 04:30 PM | ,100g | 75 |  | Levels receded | West Hartford | 212 Newington Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-07-29 | 03:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOMEOWNER | <100G | MDC PERSONEL | No |  | 2023-07-29 | 04:30 PM | <100g | 75 |  | Levels receded | West Hartford | 165 Abbotsford Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-07-27 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No |  | 2023-07-27 | 02:00 PM | < 100 GALLONS | 75 |  | Levels receded | West Hartford | 40 Loomis Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home Owner | <100g | MDC Personnel | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | Levels receded | West Hartford | 100 Oakwood Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100g | MDC PERSONNEL | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 83 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Htfd police | <10000g | MDC Personnel | Yes | Ct River | 2023-07-21 | 06:00 PM | 1000 - 25000g | 20000 |  | Levels receded | West Hartford | 200 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-07-21 | 04:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT | MDC SCADA SYSTEM | <1000 | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2023-07-21 | 09:15 PM | 1.078mg | 1078000 |  | Levels receded | West Hartford | 1 Fox Meadow Ln, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | home owner | <100g | MDC Personnel | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | M/S was flushed by jet truck. | West Hartford | 171 Still Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | home owner | <100g | MDC Personnel | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | RAIN EVENT ENDED | West Hartford | 125 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | home owner | <100g | MDC PERSONNEL | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | Levels receded | West Hartford | 64 Chelton Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100g | MDC PERSONNEL | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | West Hartford | 216 Newington Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | home owner | <100g | MDC PERSONNEL | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | West Hartford | 42 Brunswick Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-21 | 03:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100g | MDC PERSONNEL | No |  | 2023-07-21 | 06:00 PM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | West Hartford | 30 Lockwood Terrace, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 10:30AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | <100 | MDC PERSONNEL | No |  | 2023-07-16 | 05:00 PM | < 100 GALLONS | 75 |  | Bypass is eliminated once flows drop below overflow | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 02:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC Personnel | < 100 Gallons | MDC Personnel | No |  | 2023-07-16 | 05:00 PM | <100g | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | West Hartford | 29 Hall St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 10:45 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC Personnel | <100 Gallons |  | No |  | 2023-07-16 | 05:00 PM | < 100 GALLONS | 75 |  | Flow levels receded | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 03:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-07-16 | 05:00 PM | <100G | 75 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | West Hartford | 15 Greenhurst Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 10:15 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 11 MGD RATE OF DISCHARGE | SCADA | Yes | PIPER BROOK | 2023-07-17 | 12:30 PM | 7.919 MG | 7919000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-07-16 | 03:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home Owner | <100g | MDC Personnel | No |  | 2023-07-16 | 05:00 PM | <100g | 75 |  | Levels receded | West Hartford | Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 10:30AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | <100 | MDC PERSONNEL | No |  | 2023-07-16 | 05:00 PM | < 100 GALLONS | 75 |  | flows dropped below overflow level | West Hartford | 138 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 01:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC Personnel | < 100 Gallons | MDC Personnel | No |  | 2023-07-16 | 05:00 PM | < 100 Gallons | 75 |  | BLOCKAGE RELIEVED BY FLUSHING LINE WITH JET TRUCK | West Hartford | 64 Raymond Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 10:15 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 11 MGD RATE OF DISCHARGE | SCADA | Yes | PIPER BROOK | 2023-07-16 | 10:15 PM | 3.066 MG | 3066000 |  | Levels receded - Event ended | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 04:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home Owner | <100g | MDC Personnel | No |  | 2023-07-16 | 05:00 PM | <100g | 75 |  | Wet weather event ended - levels receded | West Hartford | 106 Brunswick Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 02:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC Personnel | < 100 Gallons | MDC Personnel | No |  | 2023-07-16 | 05:00 PM | <100g | 75 |  | EVENT HAS ENDED | West Hartford | 67 Southwood Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | <100 Gallons | MDC PERSONNEL | No |  | 2023-07-16 | 05:00 PM | < 100 GALLONS | 75 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 11:00 AM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Home owner | <100g | MDC personnel | No |  | 2023-07-16 | 05:00 PM | <100G | 75 |  | Surcharge - levels receded | West Hartford | 131 Somerset St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 03:45 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No |  | 2023-07-16 | 05:00 PM | <100g | 75 |  | Surcharged M/S - Wet weather event - Levels have receded | West Hartford | 1554 Asylum Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 10:15 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | RAIN 1 TO 2 INCHES PER HOUR | SCADA | 0.35 MGD RATE OF DISCHARGE | SCADA | Yes | TROUT BROOK | 2023-07-16 | 12:15 PM | .054 MG | 54000 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 02:15 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | < 1000 GALLONS | MDC PERSONNEL | Yes | TROUT BROOK | 2023-07-16 | 05:00 PM | 50000-75000g | 70000 |  | Wet weather event ended | West Hartford | 1 Fox Meadow Ln, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 12:00 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | > 100,000 MGD | MDC PERSONNEL | Yes | Webster Brook | 2023-07-16 | 05:00 PM | 54,500gal | 54500 |  | ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 121 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-16 | 12:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Resident | <100g | MDC Personnel | No |  | 2023-07-16 | 05:00 PM | <100g | 75 |  | Once elevated sewer flows recede back to normal. | West Hartford | 22 Cumberland Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 03:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No |  | 2023-07-16 | 05:00 PM | <100g | 75 |  | Once elevated sewer flows recede back to normal. | West Hartford | 160 Newington Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 01:30 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | RAIN EVENT | SCADA | 10 MGD | SCADA | Yes | TROUT BROOK | 2023-07-04 | 08:00 PM | 1.838 MG | 1838000 |  | ONCE FLOW DROP BELOW OVERFLOW LEVEL | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 04:00 PM | Lateral - Private | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 07:00 PM | < 100 GALLONS | 75 |  | ONCE FLOW DROP BELOW OVERFLOW LEVEL | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-04 | 05:00 PM | Lateral - Private | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 08:00 PM | <100 Gallons | 75 |  | Once elevated sewer flows recede back to normal. | West Hartford | 1 Fox Meadow Ln, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-04 | 05:30 PM | Lateral - Private | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 07:00 PM | < 100 Gallons | 75 |  | Once elevated sewer flows recede back to normal. | West Hartford | 358 Fern St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 05:00 PM | Lateral - Private | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 08:00 PM | <100 Gallons | 75 |  | WET WEATHER EVENT HAS ENDED - LEVELS RECEDED | West Hartford | 35 Ringgold St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 01:45 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 11 MGD | SCADA | Yes | PIPER BROOK | 2023-07-05 | 00:30 AM | 3.931 MG | 3931000 |  | Jet truck relieved M/S | West Hartford | 35 Lostbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 03:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | SCADA | 5 MGD | SCADA | Yes | TROUT BROOK | 2023-07-04 | 03:30 PM | 9,000 GALLONS | 9000 |  | elevated flow receded back to normal levels | West Hartford | 111 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 04:00 PM | Lateral - Public | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G |  | No |  | 2023-07-04 | 07:00 PM | < 100 Gallons | 75 |  | Main sewer repaired | West Hartford | 1039 Farmington Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 04:00 PM | Lateral - Private | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 07:00 PM | < 100 Gallons | 75 |  | REPAIRED LEAK ON 2 INCH SEWER FORCE MAIN | West Hartford | 1530 Boulevard, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 04:00 PM | Lateral - Public | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 07:00 PM | < 100 Gallons | 75 |  | WET WEATHER EVENT HAS ENDED | West Hartford | Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-04 | 03:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | 137ARI - STORM EVENT | HOME OWNER | 50,000 to 75,000G | MDC PERSONEL | Yes | TROUT BROOK DR | 2023-07-04 | 07:00 PM | 50,000 to 75,000G | 70000 |  | WET WEATHER EVENT ENDED | West Hartford | 828 Quaker Ln S, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-04 | 04:30 PM | Select... | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 07:00 PM | < 100 Gallons | 75 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-07-04 | 04:00 PM | Lateral - Private | Raw Sewage | Excessive Flows - Storm Event |  | HOME OWNER | <100G | MDC | No |  | 2023-07-04 | 07:00 PM | < 100 GALLONS | 75 |  | Levels have receded - Event has ended | West Hartford | 35 Ringgold St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-07-03 | 11:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Sewage Line Blockage | Homeowner | <100G | MDC Personnel | No |  | 2023-07-05 | 01:15 AM | <50g | 45 |  | Levels have receded - Event has ended | West Hartford | 7 Linnard Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-06-27 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | CSO Overflow overflowing from debris - Jet truck responding. | MDC SCADA System | 30,000 gal | MDC SCADA System | Yes | Gully brook Conduit - Gully Brook | 2023-06-27 | 11:45 AM' | 5000g | 5000 |  | MDC SEWER PERSONNEL FLUSHED MAIN SEWER AND RELIEVED BACK UP | West Hartford | 791 N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-05-20 | 09:45 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | LESS THAN 1000 GAL | MDC SCADA | Yes | PIPER BROOK | 2023-05-20 | 11:00 PM | .004 | 4000 |  | SSO DUE TO RAIN EVENT - EVENT HAS ENDED | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-05-06 | 09:15 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | ROUTINE CLEANING | 8000g | MDC PERSONNEL | No |  | 2023-05-06 | 02:15 PM | 8000g | 8000 |  | SSO DUE TO RAIN EVENT - EVENT HAS ENDED | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-05-03 | 01:00 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | LEAK ON A 2" FORCE MAIN FROM THE PUMP STATION | MDC PERSONNEL | <100 GALLONS | MDC PERSONNEL | No |  | 2023-05-03 | 02:00 PM | 50 GALLONS | 50 |  | MDC FORCES JETTED MAIN SEWER AND RELIEVED BLOCKAGE | West Hartford | 71 Caya Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-30 | 08:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA system | 9.179MG | MDC SCADA system | Yes | Piper Brook | 2023-05-02 | 00:00 AM | 9.179mg | 9179000 |  |  | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-30 | 09:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA sytem | <10000g | MDC SCADA system | Yes | TROUT BROOK | 2023-05-01 | 10:45 AM | 2.439mg | 2439000 |  | RAIN EVENT ENDED FLOWS RESIDED | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-23 | 00:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOWS - RAIN EVENT | SCADA | 4 MGD | SCADA | Yes | PIPER BROOK | 2023-04-23 | 11:30 PM | 5.28 MG | 5280000 |  | RAIN EVENT ENDED FLOWS RESIDED | West Hartford | 99 Shield St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-04-23 | 04:00 PM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure |  | MDC Personnel | 1000-5000g | MDC personnel | No |  | 2023-04-23 | 08:00 PM | <1000g | 750 |  | EXCESSIVE FLOW REDUCED WEATHER EVENT ENDED | West Hartford | 125 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-04-23 | 04:00 PM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure |  | MDC Personnel | 1000G | MDC Personnel | No |  | 2023-04-24 | 05:00 PM | <1000g | 750 |  | MDC JET TRUCK RELIEVED M/S | West Hartford | 34 Haynes Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-23 | 01:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOWS - RAIN EVENT | MDC PERSONNEL | <100 MGD | MDC PERSONNEL | Yes | Park River | 2023-04-23 | 06:00 PM | 1000-25000 | 20000 |  | Main sewer was relieved by jet truck. | West Hartford | 15 Haynes Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-23 | 01:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOWS - RAIN EVENT | MDC PERSONNEL | < 100 | MDC PERSONNEL | Yes | Trout Brook | 2023-04-23 | 06:45 PM | 1000-10000g | 9000 |  | MDC JET TRUCK RELIEVED M/S | West Hartford | 35 Haynes Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-23 | 03:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | MDC PERSONNEL | <1000 MGD | MDC PERSONNEL | No |  | 2023-04-23 | 04:45 PM | 100 GALLONS | 100 |  | MDC JET TRUCK RELIEVED M/S | West Hartford | 39 Haynes Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-04-23 | 03:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | M/S COLLAPES | HOME OWNER | <10000gal | MDC PERSONEL | No |  | 2023-04-23 | 08:00 PM | <1000g | 750 |  | RAIN EVENT ENDED - SURCHARGE RECEEDED | West Hartford | 218 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-04-23 | 03:30 PM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure | POSSIBLE SEWER COLLAPES | RESIDENT | <10000gal | MDC PERSONEL | No |  | 2023-04-23 | 08:00 PM | <1000g | 750 |  | SURCHARGE RECEEDED | West Hartford | Quaker Ln S, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-23 | 00:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOW - RAIN EVENT | SCADA | 3 MGD | SCADA | Yes | TROUT BROOK | 2023-04-23 | 07:00 PM | 2.687mg | 2687000 |  | Surcharge receded | West Hartford | 138 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-23 | 07:00 PM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure |  | Planned bypass of main sewer | No spill - Planned bypass of main sewer | No spill - Planned bypass of main sewer | No |  | 2023-04-26 | 04:00 PM | 2,070,000 gal | 2070000 |  | RAIN EVENT ENDED - SURCHARGE RECEEDED | West Hartford | 109 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-04-23 | 04:00 PM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure |  | MDC personnel | <1000g | MDC personnel | No |  | 2023-04-24 | 05:00 PM | <1000g | 750 |  | BYPASS ELIMINATED ONCE FLOWS DROP BELOWOVERFLOW | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-23 | 11:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FLOWS - RAIN EVENT | SCADA | < 100,000 GALLONS | SCADA | Yes | TROUT BROOK | 2023-04-23 | 01:30 PM | <100g | 75 |  | M/S was flushed by jet truck. | West Hartford | 11 Northbrook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-04-22 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | MDC PERSONNEL | LESS THAN 50 GAL | MDC PERSONEL | No |  | 2023-04-22 | 05:30 PM | LESS THAN 100 | 75 |  | M/S cleaned by jet truck | West Hartford | 13 Northbrook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-04-17 | 10:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | ROOTS | PASSER-BY REPORTED | <100g | MDC VISUAL INSPECTION | Yes | MILL BROOK | 2023-04-17 | 11:15 AM | <100 Gallons | 75 |  | RAIN EVENT ENDED AND EXCESSIVE FLOWS RECEDE | West Hartford | 150 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-28 | 06:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | <1000G | MDC PERSONEL | Yes | TROUT BROOK | 2023-12-28 | 08:00 PM | 3.146mg | 3146000 |  | LEVELS RECEDED | West Hartford | 60 Chelton Ave, West Hartford, CT
58042340
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-03-30 | 10:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease/Roots | MDC PERSONNEL | 500 GALLONS | MDC PERSONNEL | No |  | 2023-03-30 | 11:15 AM | 500 -1000g | 750 |  | Levels receded | Wethersfield | 111 Whippoorwill Way, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-03-15 | 11:45 AM' | Basement | Raw Sewage | Sewage Line Blockage - Other |  | HOME OWNER | <100 GALLONS | HOME OWNER | No |  | 2023-03-15 | 12:00 PM | 10 GALLONS | 10 |  | M/S flushed by jet truck | Wethersfield | 546 Wells Rd, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 06:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | LESS THAN 1000 GALLONS | MDC SCADA | Yes | TROUT BROOK | 2023-03-14 | 07:15 AM | 0.001MG | 1000 |  | Levels receded | Wethersfield | 7 Hedgerow St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 03:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | 0.013MG | MDC SCADA SYSTEM | Yes | TROUT BROOK | 2023-03-15 | 03:30 AM | 5.455MG | 5445000 |  | Levels receded | Wethersfield | 67 Lantern Ln, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 03:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | Rain Event | MDC SCADA SYSTEM | 0.036MG | MDC SCADA SYSTEM | Yes | Piper Brook | 2023-03-15 | 11:45 PM' | 15.196MG | 15196000 |  | Levels receded | Wethersfield | 16 Stockade Cir, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Snowmelt | 2023-03-04 | 12:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA SYSTEM | <10000MG | MDC SCADA SYSTEM | Yes | PIPER BROOK | 2023-03-04 | 09:45 PM | 0.840MG | 840000 |  | Levels receded | Wethersfield | 821 Folly Brook Blvd, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-02-21 | 01:30 PM | Basement | Raw Sewage | Unknown | TBD | Resident reported | <100g | MDC PERSONNEL | No |  | 2023-02-21 | 02:15 PM | <100g | 75 |  | Levels receded | Wethersfield | 61 Harmund Pl, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-02-16 | 09:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | SOFT STOPPAGE | RESIDENT REPORTED ISSUE | <10gal | MDC PERSONNEL | No |  | 2023-02-16 | 10:15 AM | LESS THAN 10g | 8 |  | Levels receded | Wethersfield | 123 Dix Rd, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-02-16 | 09:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags | PAPER | Home owner | 10 gallons | Claims agent | No |  | 2023-02-16 | 10:15 AM | 10 Gallons | 10 |  | Levels receded | Wethersfield | 58 Stillman Rd, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-02-16 | 09:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | SOFT STOPPAGE | RESIDENT REPORTED | <10gal | MDC PERSONNEL | No |  | 2023-02-16 | 10:15 AM | LESS THAN 10g | 8 |  | Levels receded | Wethersfield | Nott St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-02-16 | 09:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | SOFT STOPPAGE | RESIDENT REPORTED | <10gal | MDC PERSONNEL | No |  | 2023-02-16 | 10:15 AM | LESS THAN 10g | 8 |  | Levels receded | Wethersfield | 9 Main St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-02-13 | 02:00 PM | Manhole | Raw Sewage | Mechanical Equipment Failure | AIR VALVE ON SEWER FORCE MAIN WAS FAULTY - CORRECTIVE MEASURES TAKEN | RESIDENT REPORTED TO MDC | <100g | MDC PERSONNEL | Yes | FARMINGTON RIVER | 2023-02-13 | 03:15 PM | <100g | 75 |  | Levels receded | Wethersfield | 33 Harmund Pl, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-02-10 | 10:45 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | DAMAGE TO MAIN SEWER | EVERSOURCE EMPLOYEE | <100g | MDC PERSONEL | No |  | 2023-02-10 | 12:45 PM | <100G | 75 |  | Levels receded | Wethersfield | 123 Dix Rd, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-01-31 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | DEBRIS | Plumber | <100g | MDC claims agent | No |  | 2023-01-31 | 02:30 PM | <100g | 75 |  | Levels receded | Wethersfield | 219 Church St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 00:00 AM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure | COLLAPSE SEWER | CUSTOMER/RESIDENT | LESS THEN 100 GAL | CUSTOMER REPORTED | No |  | 2023-01-26 | 06:30 AM | <5G | 3 |  | Levels receded | Wethersfield | 106 Nott St, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 00:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 63,000 GALLONS | MDC SCADA | Yes | TROUT BROOK | 2023-01-26 | 06:00 AM | 63,000 GALLONS | 63000 |  | Levels receded | Wethersfield | 41 Deerfield Rd, Wethersfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 03:45 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | MDC EMPLOYEE | LESS THAN 1000 | MDC EMPLOYEE | Yes | WEBSTER BROOK | 2023-01-26 | 02:15 PM | 270,000g | 270000 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | Wethersfield | 44 Goodwin Park Rd, Wethersfield, CT
21816097
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-01-26 | 07:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | PASSERBY | <1000G | MDC PERSONEL | Yes | TROUT BROOK | 2023-01-26 | 02:15 PM | <1000g | 750 |  | Levels receded | Windsor | 9 Warren Ln, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 02:45 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | M/S COLLAPSE - REPAIRS COMPLETED | CUSTOMER REPORTED ISSUE | 10,000g PUMPED - NO SPILL - CONTAINED TO SYSTEM | MDC PERSONEL | No |  | 2023-01-26 | 10:30AM | 10000gal | 10000 |  | Levels receded | Windsor | 77 Green Manor Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-25 | 11:45 PM' | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 10.847 MG | MDC SCADA | Yes | PIPER BROOK | 2023-01-28 | 05:45 PM | 21.22mg | 21220000 |  | Levels receded | Windsor | 128 Custer Dr, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-25 | 11:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 5.609 MG | MDC SCADA | Yes | TROUT BROOK | 2023-01-26 | 09:15 PM | 5.722mg | 57220000 |  | Levels receded | Windsor | 503 Windsor Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-01-23 | 09:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | SCADA | < 100,000 GALLONS | SCADA | Yes | PIPER BROOK | 2023-01-24 | 01:00 AM | 2.35 MG | 2350000 |  | Levels receded | Windsor | 110 Rood Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-01-22 | 02:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Home Owner | <1000gals | visual observation by mdc claims agent | No |  | 2023-01-23 | 04:45 PM | <1000gals | 750 |  | Levels receded | Windsor | 84 Custer Dr, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-01-22 | 02:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Home owner | <100 GALS | VISUAL OBSERVATION BY MDC PERSONNEL | No |  | 2023-01-22 | 04:45 PM | <100gals | 75 |  | Levels receded | Windsor | Windsor Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-20 | 00:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 1,000 GALLONS | MDC SCADA | Yes | PIPER BROOK | 2023-01-20 | 03:00 AM | 85000 | 85000 |  | Levels receded | Windsor | 23 Green Manor Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-01-20 | 06:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Planned By-Pass due to collapsed sewer | Planned By-Pass by MDC personnel. | N/A | N/A | No |  | 2023-01-20 | 11:45 PM' | 5000 | 5000 |  | Levels receded | Windsor | 32 Scarborough Rd, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-01-20 | 02:30 PM | Basement | Raw Sewage | Unknown |  | Reported by Contractor | <10g | MDC Claims agent | No |  | 2023-01-20 | 08:30 PM | 10g | 10 |  | M/S RELIEVED BY MDC JET TRUCK | Windsor | 33 East St, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2023-01-09 | 04:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Partial pipe collapse | CONTRACTOR/plumber | <100gals | MDC PERSONNEL | No |  | 2023-01-09 | 07:30 PM | <10g | 7 |  | BACKED UP RELIEVED BY JET TRUCK | Windsor | 22 Hope Cir, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-04 | 05:00 PM | Manhole | Raw Sewage | Unknown | TBD | LOCAL RESIDENT | <100g | MDC PERSONEL | Yes | ROCKHOLE BROOK | 2023-01-04 | 06:30 AM | 25000-50000gals | 40000 |  | REPAIRS MADE BY MDC CREWS | Windsor | 634 Stone Rd, Windsor, CT
POQUONOCK WPCF (MDC WINDSOR) | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 02:30 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Distribution tower which feeds the Trickling Filters overflowing.Primary Effluent pumps protecting a | High Level alarm | 60,000 gph for 6 hours | Recalculated using weir overflow calculation | Yes | Farmington River | 2023-01-26 | 08:15 AM | ~352,400 gallons | 352400 | Influent flow rate change |  | Windsor | 1222 Poquonock Ave, Windsor, CT
81283992
[17 empty] | TOTAL VOLUME | 320767219

## MERIDEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MERIDEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-18 | 11:45 AM' | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Heavy rains over a short duration caused flows into Harbor Brook Pump Station to increase beyond wha | SCADA Alarm | 370,000 gals. | Flow meter | Yes | Quinnipiac River | 2023-12-18 | 05:45 PM | 990,000 gals. | 990000 |  | storm event ended and flows subsided | Meriden | 226 Evansville Ave, Meriden, CT
MERIDEN | Closed | Sewage Bypass | Dry | 2023-05-14 | 08:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Private lateral owned by Townline Plaza that runs through a right of way clogged, causing a backup a | citizen complaint | less than one gallon a minute | visual observation | No | dry storm culvert that leads to meetinghouse brook | 2023-05-15 | 04:00 PM | Approx 1,300 gals | 1300 |  | Townline Plaza Owners called in an environmental company to jet and clean their lines. | Meriden | 185 Old Stagecoach Rd, Meriden, CT
MERIDEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-01-26 | 07:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | homeowner notified | 75 gallons | visual | No |  | 2023-01-26 | 08:15 AM | 75 gallons | 75 |  | cleaning was performed and flows are subsiding | Meriden | 46 Orchid Rd, Meriden, CT
[17 empty] | TOTAL VOLUME | 991375

## MIDDLETOWN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MIDDLETOWN WPCA | Closed | Sewage Bypass | Dry | 2023-05-31 | 02:15 PM | Lateral - Private | Raw Sewage | Unknown |  | foul odor | minimal | visual | No |  | 05/31/2023 | 04:00 PM | 30 gallons | 30 |  |  | Middletown | 1 Dove Ln, Middletown, CT
[17 empty] | TOTAL VOLUME | 30

## MILFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MILFORD - BEAVERBROOK | Closed | Sewage Bypass | Dry | 2023-11-28 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Publics works called Sewer Dept, water on the road | 1,000 gallons | guestimate | No |  | 2023-11-28 | 11:00 AM | 10,000 gallons | 10000 |  | Fixed force main pipe | Milford | 222 3rd Ave, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-11 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Observation | Currently flowing at 19 MGD | Flow Meter | Yes | Housatonic | 2023-12-12 | 09:00 AM | 8.000 gallons | 8000 |  | Storm ended | Milford | 1255 Oronoque Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-05-01 | 06:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | solids in the final effluent due to rain and high flows | solids in the effluent from sending out a sample for testing nitrogen | N/A | by sample test run | No |  | 2023-05-01 | 07:30 AM | N/A | 0 |  | adding polymer and holding solids in tanks | Milford | 1225 Oronoque Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2023-04-25 | 06:00 AM | Sewer Main | Raw Sewage | Unknown |  | Call from police | 5-10 gallons | estimate | No |  | 2023-04-25 | 07:00 AM | 10 gallong | 10 |  | jet line followed by CCTV | Milford | 1255 Oronoque Rd, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2023-02-11 | 08:45 AM | Basement | Raw Sewage | Unknown | CCTV on 2/14/2022 | Fire Department Called | 20 gallons | estimate | No |  | 2023-02-11 | 08:00 PM | 20 gallons | 20 |  | Cleared blockage with jet truck. | Milford | 180 Melba St, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-01-26 | 06:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | high flows due to rain event. caused blankets in the final tanks to be higher than normal | walking out to the final overflow weirs and seeing the final effluent | unable to verify | unable to verify | Yes | Housatonic river | 01/26/2023 | 02:00 PM | 5,000 gallons | 5000 |  | Storm ended | Milford | 1255 Oronoque Rd, Milford, CT
[17 empty] | TOTAL VOLUME | 23030

## MONTVILLE
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MONTVILLE | Closed | Sewage Bypass | Rain greater than 4" per hour | 2023-12-18 | 11:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event leading to poor treatment (due to hydraulic overload/short detention times). An increase | Effluent (direct) inspection showed some MLSS intermittantly escaping from process tanks (SBRs) duri | 50-100,000 mg | estimated due to intermittant discharge with observed solids | Yes | Horton's Cove/Thames River | 2023-12-21 | 02:30 PM | 50-100,000 mg | 75000 |  | rain caused I/I flow eased to close to normal conditions (influent) | Montville | 83 Pink Row, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2023-09-16 | 10:30AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | n/a | Report into call phone that a stream of water on Route 32 observed by driver in dry conditions. | 2000 gallons | visual inspection | No | n/a | 2023-09-16 | 11:00 AM | 500 gallons | 500 |  | Bypass via pumper truck. Repair of force main. | Montville | 2549 Norwich-New London Turnpike, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2023-08-04 | 12:30 PM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | Odors would indicate some type of seepage from private sewer line at intersection of Route 32 and De | Odor complaint. Investigation by WPCF staff and subcontractors. | 100 gallons- enough to cause odors. No leakage found. | Estimate. | No | n/a | 2023-08-07 | 03:45 PM | 500 gallons | 500 |  | Bypass RWCB discharge line to municipal system via Xylem (Godwin) setup. | Montville | 2 Depot Rd, Montville, CT
[17 empty] | TOTAL VOLUME | 76000

## NAUGATUCK
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 10:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Collection system employee | 50-100 gallons per minute | estimated visually | Yes | Naugatuck | 2023-12-19 | 01:00 AM | 67,500 | 67500 |  | flows started to subside | Naugatuck | 2 Cotton Hollow Rd, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2023-11-17 | 08:00 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure |  | Police Officer | 500+ | Visual estimation | Yes | Storm catch basin | 2023-11-17 | 12:00 PM | approximately 300 | 300 |  | force main repaired | Naugatuck | 5 Inwood Dr, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2023-10-01 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Public works found it | 300-500 | Visual rate of flow | No |  | 2023-10-01 | 11:30 AM | 400 | 400 |  | hole on top of pipe was how the rocks entered. Pipe is being repaired | Naugatuck | 607 Rubber Ave, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2023-03-01 | 07:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Public Works | 500-1000 | Visual flow to one minute time | No |  | 2023-03-01 | 08:00 AM | 500-1000 | 750 |  | Jetting and vactor | Naugatuck | 302 High St, Naugatuck, CT
[17 empty] | TOTAL VOLUME | 68950
Private Property Bypass - not counted in totals
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2023-09-06 | 08:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | After further investigation it was discovered the roots are coming out of a lateral. Unknown if it i | By the home owner. | 100 to 300 gallons | By eye sight | No |  | 2023-09-06 | 10:00 AM | up to 300 gallons | 300 |  | Homeowner will call in contractor for cleanup | Naugatuck | 27 Morning Dove Rd, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2023-03-06 | 05:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Resident reported that they couldn’t use their facilities. | 0 | Nothing was seen. | No |  | 2023-03-06 | 06:15 PM | 0 | 0 |  | Vactor and Jetting. Line CCTV'd | Naugatuck | 173 Crestwood Dr, Naugatuck, CT

## NEW LONDON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2023-12-18 | 10:30AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Call in from home owner | Less than 7,500 gallons. Crews were near by and able to shut down pumpstation shortly after bypass b | Pumping times from pumping station. | Yes | Thames River | 2023-12-18 | 00:00 AM | Less than 7,500 gallons | 7250 |  | Replaced 12' of 12" sewer main. Plans are in place to replace rest of 12" sewer main in that area. | New London | 984 Pequot Ave, New London, CT
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2023-12-11 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Home owner called to report water main break. After shutting down distribution system we realized ou | 12,622.8 gallons | Amount estimated by using crack measurements and converting to cubic feet. Then multiplying by 7.48 | Yes | Thames River/Long Island Sound. Storm outfall loation is right at the mouth of the Thames River wher | 2023-12-11 | 02:30 PM | 12,622.8 gallons | 12623 |  | Septage truck loading, vac truck pumping, and pumping to the nearest gravity sewer. Force Main had a | New London | 979 Pequot Ave, New London, CT
NEW LONDON STP | Closed | NPDES Permitted Bypass of Secondary Treatment | Dry | 2023-04-09 | 10:30 PM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | Broken Valve | Flooded pump room | 30gpm | scada trends | Yes | Bentley creek/Thames river | 2023-04-10 | 02:30 AM | approximately 100gal | 100 |  | ball valves with safety locks that cant be forced open. | New London | 100 Trumbull St, New London, CT
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2023-03-11 | 04:00 PM | Treatment Plant | Sludge Spill | Mechanical Equipment Failure | Check ball cap on piston pump sheared a bolt causing the cap to loosen and come off. Sludge back flo | Operator doing plant rounds. | Unable to estimate at this time. | N/A | No |  | 2023-03-11 | 04:45 PM | Not determined. All sludge collected in vac truck and sent back to head works of the STP. | 100 |  | Operator and road crew crew used a vac truck and hoses to clean up sludge. | New London | 100 Trumbull St, New London, CT
[17 empty] | TOTAL VOLUME | 20073

## NEW MILFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW MILFORD | Closed | Sewage Bypass | Dry | 2023-07-12 | 10:45 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Mud, Rags and debris blocking flow in a 8" gravity line. | Department of New Milford Public works notified Sewer Department of water flowing into street. | 25 GPM for 65 Mins =1625 Gallons. | SSCSC Manhole Overflow Gauge. | Yes | Great Brook | 2023-07-12 | 11:45 AM' | 1625 Gallons | 1625 |  | Crew immediately flushed line with jetter. Contractor repaired Broken pipe. | New Milford | 41 Hill Dr, New Milford, CT
[17 empty] | TOTAL VOLUME | 1625

## NEWTOWN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEWTOWN W P C F | Closed | Sewage Bypass | Dry | 2023-06-05 | 08:30 AM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | coupling failed | Brian was the one to discover and shut down | 0 - it was all contained |  | No |  | 2023-06-06 | 11:00 AM | 0 | 0 |  | yes, repair was completed | Newtown | 24 Commerce Rd, Newtown, CT
[17 empty] | TOTAL VOLUME | 0
Private Property Bypass - not counted in totals
NEWTOWN W P C F | Closed | Sewage Bypass | Dry | 2023-06-26 | 11:15 AM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure |  | Received call from answering service (Accurate Answer) | less than 500 gallons | eyeball, a 4 foot x 4 foot area | No |  | 2023-06-26 | 02:00 PM | 0 |  |  | Verdi construction did the repair | Newtown | 47 Church Hill Rd, Newtown, CT

## NORTH HAVEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2023-11-28 | 00:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | CONTRACTOR HIT A MANHOLE STRUCTURE ON FROMTAGE ROAD AND MONTOWESE CAUSING DIRT TO BACKFILL THE INTER | CONTRACTOR NOTIFIED THE TOWN IMMEDIATELY | < 50 GALLONS, | VISUAL ESTIMATE | No |  | 2023-11-28 | 02:30 PM | estimated 50 gallons or less | 50 |  | STAFF JET CLEANED THE INTERCEPTOR LINE AND THE CONTRACTOR REPAIRED THE DAMAGEDMANHOLE | North Haven | N Frontage Rd, North Haven, CT
[17 empty] | TOTAL VOLUME | 50

## NORWALK
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-12-28 | 01:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event |  | Homeowner Reported it. | Less than 500 gallons. | Amount recovered in VAC truck | No |  | 2023-12-28 | 12:15 PM | Less than 500 gallons | 450 |  | Area cleaned. | Norwalk | 29 Willow St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-29 | 01:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | Phone call from homeowner | Unknown at this time | Unknown at this time | Yes | Norwalk River | 2023-09-29 | 03:00 PM | Unknown, this area of the city was experiencing flash flooding. | 3000 |  | Waters receded and rainfall softened. | Norwalk | 3 Armstrong Ct, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-09-29 | 12:15 PM | Treatment Plant | Partially Treated Raw Sewage | Mechanical Equipment Failure |  | SCADA system alarm | Less than 100 out of containment | To be determined | No |  | 2023-09-29 | 12:30 PM | Lees than 100 gallons outside of containment. | 75 |  | Electronic glitch is being investigated by a vendor. | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-08-28 | 08:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Resident Called in. | <100 Gallons |  | No |  | 2023-08-28 | 08:30 AM | <100 gallons | 75 |  | Line was jetted and vacuumed out. | Norwalk | 27 Priscilla Rd, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-08-01 | 10:15 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by first district water | 50 gallons | Visual | No |  | 2023-08-01 | 11:15 AM | Under 50 gallons | 30 |  | Line was cleaned and cleared | Norwalk | 25 New Canaan Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-07-29 | 12:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | FOG and Roots | police dept | less than 500 | visually | No |  | 2023-07-29 | 12:30 PM | Under 100 gallons | 75 |  | Line was cleaned and cleared. | Norwalk | 474 Main Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-14 | 10:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | High-flow secondary scum well pumps could not keep up with the flow into it from final tank scum t | Hi alarm when the operator saw the well overflowing into the overflow tank he immediately closed the | Not known at this time | To be determined by the holding tank level | No |  | 2023-07-14 | 10:15 AM | under 100 gallons | 75 |  | The area was cleaned and drained. | Norwalk | 15 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-05-08 | 11:00 AM | Treatment Plant | Sludge Spill | Other | Drain Clogged in the thickener | Employee saw sludge coming out of the thickener tank. | 1000 - 2000gals 10 to 40gal/min | eyesight. and Vac truck loads | No |  | 2023-05-08 | 11:15 AM | approx. 1000 Gallons | 1000 |  | Drain was cleared, and spill was completely cleaned. | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-03-11 | 11:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Construction debris in manhole invert | by resident | less then 50 gallons | visual inspection | No |  | 2023-03-13 | 11:30 AM | Less than 50 gallons | 30 |  | Area was cleaned. Line was jetted and debris vacuumed out. | Norwalk | 155 W Cedar St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-02-01 | 12:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Mechanical Equipment Failure | Yard Hydrant was found with an underground leak. | Routine plant inspection | 500 gallons | Visually until our team cleans area up. | No |  | 2023-02-01 | 12:15 PM | 500 gallons | 5000 |  | Visually until our team cleans area up. | Norwalk | 60 S Smith St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2023-01-29 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Resident Reported it. | Less than 50 gallons | Visual spill around manhole and amount recovered by vac truck | No |  | 2023-01-29 | 01:45 PM | Less than 50 gallons. | 30 |  | Line was cleaned and flow was restored. | Norwalk | 27 Ivy Pl, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 11:45 PM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Heavy Rain. | Visually poor effluent. | unknown | Waiting for TSS results from Lab. | Yes | Norwalk River | 2023-01-26 | 02:15 AM | The flow during that time was 3.77 MGD | 5000 |  | When rain subsided and flow decreased the effluent quality improved. | Norwalk | 60 S Smith St, Norwalk, CT
[17 empty] | TOTAL VOLUME | 14840

## NORWICH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-12-08 | 09:30 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | Station programming was being changed to minimize hard stops on the pump. When changing the program | CSO email alert at 3:12PM | 2736 | CSO flow meter | Yes | Thames River | 2023-12-08 | 09:45 AM | 2736 | 2736 |  | reconnected VFD to Controller | Norwich | 190 S Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-12-08 | 04:30 PM | Manhole | Raw Sewage | Other | Bypass hose for forechain was cut. | Call to control room | 5 GPM when station turns on | Visual Estimate-Station turned off so repairs could be made. | No | Thames | 2023-12-08 | 09:00 PM | 48206 | 48206 |  | Replaced flex line on bypass. | Norwich | Laurel Hill Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-12-02 | 07:00 AM | Treatment Plant | Sludge Spill | Other | New driver for dry sludge cake hauler spilled roughly 1/2 yard of dry sludge while lifting container | Operator doing morning rounds | 1/2 yard of dry cake | Visual estimate | No |  | 2023-12-02 | 07:00 AM | estimated 1 yard of dry sludge cake | 1 |  | Cleaned up with sewer vac and disposed of in influent channel. Spoke to hauler about making sure we | Norwich | 52 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-11-30 | 07:00 AM | Treatment Plant | Sludge Spill | Other | Dry sludge cake, spilled when hauler picked up roll off container. About 1/2 yard | Driver called in to control room | 1/2 yard dry cake on pavement | visual estimate | No |  | 2023-11-30 | 09:15 AM | 1/2 yard of dry sludge cake. | 1 |  | Dry sludge vacuumed up with sewer Jet/Vac and dumped in influent channel. | Norwich | 52 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-11-28 | 09:00 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | While doing our monthly generator load testing a breaker tripped causing a power failure when return | FAS-CSO flow meter | 29466 Gallons | Flow meter | Yes | Thames River | 2023-11-28 | 10:30AM | 29466 Gallons | 29466 |  | Reset Breaker | Norwich | 228 S Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-10-26 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Unknown at this time | Called in | Unknown at this time. >5 gallons per min. | Visual estimate per operators on scene | No |  | 2023-10-27 | 07:30 PM | 28305 | 28305 |  | Force main is on bypass. | Norwich | Laurel Hill Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-09-19 | 12:30 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Pump tripped out due to something trapped in the pump. | While cleaning the station it made an odd noise and the technician noticed the pump shut down. | 4404 | CSO-flow meter | Yes | Shectucket | 2023-09-19 | 12:45 PM | 4404 | 4404 |  | Started other pump. | Norwich | 8 City Landing, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-08-11 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Station went airbound when cleaning the sewer wetwell causing water hammer to the FM. | Customer Call | 10 GPM. Prior to shutting station off. | Visual Estimate+ Flow Meter | Yes | Thames River | 2023-08-11 | 11:00 PM | 349647 | 349647 |  | Replaced 22'' of sewer force main. | Norwich | 134 Chelsea Harbor Dr, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-04-27 | 07:00 PM | Pump Station | Raw Sewage | Sewage Line Blockage - Grease | Large mass of grease covering the entire grate | CSO flow meter |  |  | Yes | Shectucket River | 2023-04-27 | 08:00 AM | 15581 Gallons | 15581 |  | Raked hole in grate, then used sewer jet to Vac grease out. | Norwich | 8 City Landing, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-04-10 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Employee drive by | 100 gallons | Visual estimate | No |  | 2023-04-10 | 12:15 PM | 100 gallons | 100 |  | Vac’ed manhole and jetted main/service | Norwich | 180 Central Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-04-04 | 08:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Customer call | 100 Gallons | 100 Gallons | No | n/a | 2023-04-04 | 09:45 AM | 100 Gallons | 100 |  | Raked Rags from manhole 0641- Then jetted and cleaned main. | Norwich | 561 W Main St, Norwich, CT
[17 empty] | TOTAL VOLUME | 478547
Private Property Bypass - not counted in totals
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-09-28 | 09:15 PM | Lateral - Private | Raw Sewage | Unknown | Visual remains of a backup in the homeowner's yard. Advised him owner they need to get a plumber to | Customer call | overflows when water is used | visual estimate | No |  | 2023-09-28 | 10:00 AM | 10 Gallons |  |  | Customer had contractor clean and video the line. Customer emailed report to NPU. | Norwich | 69 Boswell Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2023-05-30 | 06:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other |  | Customer call | 1-2 GPM | visual estimate | No |  | 2023-05-31 | 02:30 AM | 200 gallons |  |  | Owner calling in a contractor to jet line and remove asphalt. | Norwich | 224 Salem Turnpike, Norwich, CT

## OXFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
OXFORD | Closed | Sewage Bypass | Dry | 2023-10-16 | 09:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Deteriorating pipe | Discovered by staff doing daily rounds | 40,000 | Length of pipe that drained out | Yes | little river | 2023-10-16 | 12:00 PM | 45,000 | 45000 |  | Replace bad piece of pipe | Oxford | 50 Towner Ln, Oxford, CT
OXFORD | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-26 | 08:15 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Break in 10" Force Main | Discovered upon daily Inspection @ 8:15 AM | 45,000 about | 9 hrs @ 5,000 per hr =50,000After looking over pump run times it looks like the break happened at ab | Yes | Little River | 2023-09-26 | 11:00 AM | 45,000 | 45000 |  | Removed damaged pipe and installed new pipe | Oxford | 46 Towner Ln, Oxford, CT
[17 empty] | TOTAL VOLUME | 90000

## PLAINFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2023-04-10 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | large rock found in manhole blacking the sewer main. | property owner noticed sewer leaking out of manhole in the grass along the side of the property | 100-500 gallons | onsite estimation | No |  | 2023-04-11 | 01:00 PM | 400 gallons | 400 |  | Jetted the sewer main, then vacuumed out sewage from the blocked manhole. Rock was removed from manh | Plainfield | 13 West Pkwy, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-25 | 02:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | High Flows due to rain event on the 1/25/23 & 1/26/23 caused plant to be over the design capacity of 1.08 MGD. Influent flows on 1/25 were 1.47 MGD and on 1/26 were 1.88 MGD | Visual | TBD | Meter | Yes | Moosup River | 2023-01-27 | 03:00 PM | 1.19MG | 1190000 | Meter | Enacted high rain protocol | Plainfield | 26 Black Hill Rd, Plainfield, CT
[17 empty] | TOTAL VOLUME | 1190400

## PLYMOUTH
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2023-12-04 | 02:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | pin hole in top of pipe | Incident was called in to WPCA | approx. 500 gallons | 2 gpm for approx. 4 hours | No |  | 2023-12-04 | 06:00 PM | approximately 500 gallons | 500 |  | contractor repaired pipe with sleeve, vac truck emptied forcemain | Plymouth | 221 South St, Plymouth, CT
[17 empty] | TOTAL VOLUME | 500

## PORTLAND
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
PORTLAND | Closed | Sewage Bypass | Dry | 2023-02-22 | 01:00 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure |  | An alarm went off about a pump failure at our Coe Ave pump station. Pump #2 is currently being repai | 300GPM | Pump capacity. | No |  | 2023-03-03 | 08:30 AM | 225,000 gallons | 225000 |  | Rebuilt 1 of the 2 submersible pumps. | Portland | 138 Middlesex Ave Ext, Portland, CT
[17 empty] | TOTAL VOLUME | 225000

## RIDGEFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
RIDGEFIELD (RT7), TOWN OF | Closed | Sewage Bypass | Dry | 2023-09-05 | 07:00 AM | Treatment Plant | Raw Sewage | Mechanical Equipment Failure | Large mass of rags/wipes overloaded Comminutor and caused it to trip off. | Operator on duty. | 100 gallons | Visual | No | Little Pond | 2023-09-05 | 09:00 AM | 100 gallons | 100 | Visual | Clog removed | Ridgefield | 901 Ethan Allen Hwy, Ridgefield, CT
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2023-11-14 | 02:00 PM | Treatment Plant | Raw Sewage | Other | Someone on the job site turned off the two new wet well pumps and the contractor's diesel backup gen | Operator noticed pumps had been turned off and high-level alarm came on. | <250 gallons. | visual estimate | No |  | 2023-11-14 | 02:15 PM | <250 gallons | 200 |  | Pumps were put back into auto and the backup diesel pump was repaired. | Ridgefield | 22 South St, Ridgefield, CT
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2023-06-02 | 06:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | There was a blockage in the line caused by grease. | This was called into our after hours answering service by someone that noticed water coming out of t | <300 gallons | By the amount coming out of the manhole and the duration of the event. This is also a very low flow | Yes | Ridgefield Brook by wat of storm drain. | 2023-06-02 | 07:15 PM | <300 gallons | 250 |  | The line was cleaned using our vactor/jet truck. | Ridgefield | 103 Danbury Rd, Ridgefield, CT
[17 empty] | TOTAL VOLUME | 550

## ROCKY HILL (MDC)
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
ROCKY HILL WPCF (MDC) | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-25 | 03:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Plant operator identified initial raw sewage bypass from headworks. | Initial raw sewage bypass = 900 gallonsDisinfected partially treated raw sewage bypass calculated to | Estimated visually and calculated using SCADA flow readings | Yes | Connecticut River | 2023-09-25 | 05:00 PM | 900 gallons of raw sewage into catch basin and then into stormwater swale.51800 gallons of disinfect | 900 |  | By closing the secondary bypass valve at 5:05pm and influent flows decreasing. | Rocky Hill | 80 Goff Brook Ln, Rocky Hill, CT
[17 empty] | TOTAL VOLUME | 900

## SIMSBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2023-06-06 | 08:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | Found root mass blocking line inside manhole. | Business owner report | 150 Gallons | estimated based on flow | Yes | Farmington River | 2023-06-06 | 09:45 AM | 150 Gallons | 150 |  | removed root mass from invert | Simsbury | 3 Tunxis Rd, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2023-06-06 | 08:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Roots |  | Phone call from resident | 150 gallons | trickle into catch basin seemed to be about 1gal/min | Yes | Farmington River | 2023-06-06 | 09:45 PM | 150 gallons | 150 |  | removed root mass | Simsbury | 7 Tunxis Rd, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-22 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Reported by building management company Canal Place | 2 GPM | Esitmated by quantity in basements | No |  | 2023-01-22 | 10:00 PM | 150 gallons | 150 |  |  | Simsbury | 30 Old Canal Way, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-22 | 06:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease buildup in area leading to syphon | reported by homeowners | 2 gpm based on amount flowing into basements | visual estimate | No |  | 2023-01-22 | 11:45 PM' | 750 gallons | 750 |  | Main sewer line was jetted and cleared of grease | Simsbury | 155 Hopmeadow St, Simsbury, CT
[17 empty] | TOTAL VOLUME | 1200

## SOUTH WINDSOR
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTH WINDSOR | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 08:00 AM | Basement | Raw Sewage | Electrical Equipment Failure | The PLC, which is the brain of the pump station, became locked into position and both pumps at the s | Resident called the police and public works. | 28000 gallons | I used the treatment plant flow at the time (3.5 mgd) and that station handles about 15% of the Town | Yes | Avery Brook. Some sewage made it into the storm sewer but the majority ended up in the homeowners b | 2023-09-25 | 09:15 AM | About 28000 gallons | 28000 |  | We were able to put the station in hand and get it pumped down and then eventually got the PLC back | South Windsor | 115 Pine Tree Ln, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-09 | 05:30 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | Power outage | Through the SCADA system | About 37000 gallons | It took 10 minutes for UV to come back up on generator and we were flowing 2.84 MGD when the power l | Yes | Connecticut River | 2023-09-09 | 07:30 PM | About 37000 gallons | 37000 |  | Power was restored | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-06-04 | 04:45 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | Power outage. Power loss to UV, after generator kicked on it took about 20 minutes to get bulbs bac | SCADA Alarms | 36,666 gallons | Flow at time of outage was 2.64 MGD and we were down for about 20 minutes, I just did the calculatio | Yes | Connecticut River | 2023-06-04 | 05:00 PM | 36,666 gallons | 36666 |  | Bulbs came up to full strength, power restored | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-06-02 | 04:00 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | Power loss. UV shut down when switching to generator power so it took 15 minutes to fully come back | SCADA Alarms | 32604 gallons | 3.13 MGD flow rate for approximately 15 minutes | No | Connecticut River | 2023-06-02 | 04:15 PM | 32604 gallons | 32604 |  | The bulbs came up to full strength and power was restored | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-19 | 01:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Blockage caused by silt in the sewer line. | Resident was getting wastewater in the basement and alerted police. | Unknown | NA | No |  | 2023-01-19 | 02:15 PM | Unknown | 30 |  | Cleared blockage with jetted truck | South Windsor | 549 Ellington Rd, South Windsor, CT
[17 empty] | TOTAL VOLUME | 134300

## SOUTHINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTHINGTON | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 01:30 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Plant SCADA system notified staff that the bypass valve automaticly opened | 4400 Gallons | Flow Meter | Yes | Quinnipiac River | 2023-12-18 | 01:45 PM | 4400 Gallons | 4400 |  | Plant staff manually closed the valve and diverted excessive flows to an empty clarifier | Southington | 999 Meriden-Waterbury Turnpike, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-30 | 11:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Alarm system notified plant staff of a high wet well in the Denitrification Building. |  |  | Yes | Quinnipiac River | 2023-09-30 | 01:45 PM | 262,000 gallons | 262000 |  | Plant flows began to recede and plant staff were able to close the bypass valve. | Southington | 999 Meriden-Waterbury Turnpike, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-25 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Alarm system notified plant staff of a high wet well in the Denitrification Building. | 43,000 gallons | Flowmeter in Denitrification Building | Yes | Quinnipiac River | 2023-09-25 | 11:00 PM | 43,000 gallons | 43000 |  | Plant staff were able to slow down the flow entering the Denitrification Building to allow the wetwe | Southington | 999 Meriden-Waterbury Turnpike, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2023-09-14 | 10:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Highway Department was mowing and discovered the water exiting the manhole. | 50-100 gallons | Estimate | No |  | 2023-09-14 | 11:30 AM | 50-100 gallons | 75 |  | Plant staff removed sticks from the sewer main that was causing the blockage. | Southington | 776 Woodruff St, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2023-07-20 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | Company called the Town of Southington WPCF and notified plant staff of water exiting a manhole on t | 50 gallons | Estimate | No |  | 2023-07-20 | 11:45 AM' | 50 gallons | 50 |  | Plant staff had to vacuum material from the sewer main to relieve the blockage. Plant staff took sam | Southington | 45 Newell St, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2023-06-23 | 09:45 AM | Lateral - Public | Raw Sewage | Other | Contractor was excavating for another utility and accidentally hit a resident's sewer lateral. | Contractor was excavating and noticed a pipe. | 2 gallons | Estimate | No |  | 2023-06-23 | 10:30AM | 2 gallons | 2 |  | Contractor repaired the damaged sewer lateral. | Southington | 1165 Old Turnpike Rd, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2023-04-05 | 05:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Resident called and mentioned there was water in their basement. | 2 gallons (estimated quantity) | Estimate | No |  | 2023-04-05 | 05:15 PM | 2 gallons | 2 |  | Town of Southington WPC jetted the line to remove the blockage. | Southington | 42 Knox Dr, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2023-02-15 | 03:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Resident noticed water coming out of manhole. | 100 gallons | Estimate | No |  | 2023-02-15 | 03:00 PM | 100 gallons | 100 |  | Southington WPC staff jetted the sewer main to relieve the blockage. | Southington | 5 Pond Mill Rd, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2023-02-06 | 10:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Resident called because there was water in their basement. | 100 gallons | Estimate | No |  | 2023-02-06 | 11:00 PM | 100 gallons | 100 |  | Town of Southington WPC staff jetted the sewer main to relieve the blockage. | Southington | 90 Old Turnpike Rd, Southington, CT
[17 empty] | TOTAL VOLUME | 309729

## SOUTHBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2023-04-06 | 04:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Seepage | 2 gallon/hour total flow estimated as 20 gallons | Visual estimate | No |  | 2023-04-06 | 06:00 PM | 20 gallons | 20 |  | Station was shut down and pumped out. The line was located and repaired. | Southbury | 258 Heritage Village, Southbury, CT
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2023-04-06 | 04:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Employee doing CBYD markout | 2 gallons/hour estimated 20 gallons total. | Visual estimate | No |  | 2023-04-06 | 05:00 PM | 20 Gallons | 20 |  | Replaced PVC pipe and coupling | Southbury | 158 Poverty Rd, Southbury, CT
[17 empty] | TOTAL VOLUME | 40

## STAFFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STAFFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-07-16 | 11:45 AM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | The operators on site, On-standing by for the storm | Unknown at this time | Unable to calculate at this time | Yes | Willimantic River | 2023-07-16 | 01:15 PM | 250,000 gallons | 250000 |  | Higher polymer rate into clarifiers, shut off the air in the last aeration tank zones, and flow redu | Stafford | 50 River Rd, Stafford, CT
STAFFORD | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-07-04 | 01:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | On-call operator monitoring the facility | Estimated 150,000 gals | Flow is entering the plant at 3.5MGD/24 hours | Yes | Willimantic River | 2023-07-04 | 02:30 PM | 182,375 gals | 182375 |  | Shut off aeration tank zone 3, added polymer to clarifiers, and Blankets in clarifiers settled from | Stafford | 50 River Rd, Stafford, CT
[17 empty] | TOTAL VOLUME | 432375
Private Property Bypass - not counted in totals
STAFFORD | Closed | Sewage Bypass | Dry | 2023-10-19 | 03:30 PM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | The vacant house's lateral plumbing pipe was broken off at the foundation. | Sewer smell in the area | 10-12 gals a min for an undetermined amount of time | Approximate number of house connections times average gallon flow per day. Unknown length of time s | Yes | Rhode Island Millponds | 2023-10-19 | 04:15 PM | Unknown. | 0 |  | The main sewer line was jetted, and the owner was ordered to repair the open lateral pipe in the vac | Stafford | 3 Park St, Stafford, CT

## STAMFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STAMFORD | Closed | Sewage Bypass | Dry | 2023-12-21 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | A sanitary sewer overflow(SSO) was reported to WPCA from City of Engineering at the intersection of | WPCA was notified by the City Engineering Department. | 30-gallons | Wetted area was estimated. | No |  | 2023-12-21 | 12:00 PM | Approximately, 30-gallons. | 30 |  | Main sewer line and private lateral are being repaired. | Stamford | Lockwood Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2023-10-10 | 01:15 PM | Treatment Plant | Raw Sewage | Sewage Line Broken by Contractor or other utility | Contractor excavations to expose the 18" Thickener Overflow line returning to the Primary Distributi | Constuction crew reported to SWPCA Foreman. | 18" line leaking an estimated 694 gpm for 15 - 20 minutes. Total estimated as 15,000 gallons of unt | Estimate of flow in 18" line | Yes | Entered storm drain system leading to Stamford's East Branch Harbor to Long Island Sound. | 2023-10-10 | 01:30 PM | Estimated at 15,000 gallons | 15000 |  | Primary tanks and Thickener tanks removed from service and flow allowed to aeration for treatment un | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2023-08-23 | 10:45 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | A break in the 10" Ductile Iron force main. | Reported to WPCA from another City Department. | 20 gals. intermittently discharged | Wetted area was estimated. | No |  | 2023-08-24 | 05:30 PM | Contained and removed approximately 720 gallons | 720 |  | Reported to WPCA from another City Department. | Stamford | 315 Ocean Dr W, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2023-03-27 | 01:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Unknown | Another City Department reported the observation. | Intermittent discharge rate 12GPM. | Wetted area and pump rates were estimated. | No |  | 2023-03-27 | 02:30 PM | 48 gallons | 48 |  | Approximately 13 feet of 10" diameter ductile iron pipe force main was replaced with new pipe. | Stamford | Ocean Dr W, Stamford, CT
[17 empty] | TOTAL VOLUME | 15798

## STONINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STONINGTON - MYSTIC | Open | Sewage Bypass | Rain less than 1" per hour | 2023-12-28 | 09:15 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Manhole overflow | 25,000 gallons discharged | Calculated the volume of the pipe connecting the break to the pump station from which it drained bac | No |  | 2023-12-28 | 03:30 PM | 25,000 gallons discharged | 25000 | Calculated the volume of the pipe connecting the break to the pump station from which it drained back. | Pipe repaired | Stonington | Broadway Ave Ext, Stonington, CT
STONINGTON - MYSTIC | Open | Sewage Bypass | Dry | 2023-10-17 | 12:00 PM | Treatment Plant | Raw Sewage | Other | A hole/leak was discovered in the bottom of the grit removal system. | Operator on shift discovered it. | 50 Gallons | Operator had to scoop the grit that leaked through back into the hopper it usually dumps into. They | No |  | 2023-10-17 | 04:00 PM | 50 Gallons | 50 | Operator had to scoop the grit that leaked through back into the hopper it usually dumps into. They estimated based off the amount they had scooped back into the hopper. | Hole Repaired | Stonington | 22 Edgemont St, Stonington, CT
STONINGTON-BOROUGH WPCF | Closed | Sewage Bypass | Dry | 2023-03-10 | 12:15 PM | Treatment Plant | Sludge Spill | Other | Overflowed sludge truck while loading. | Discovered by plant operator. | N/A- currently evaluating | Flow rate of pump | No |  | 2023-03-10 | 01:45 AM | 200 gallons | 200 |  | Contained and road crew cleaning up the mess. Disinfect the area. | Stonington | 2 High St, Stonington, CT
[17 empty] | TOTAL VOLUME | 25250

## STRATFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STRATFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-11 | 04:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | 3 1/2" of rain | Low UV dosage alarm | Approx. 23MGD | SCADA trend | Yes | Housatonic River | 2023-12-11 | 10:30AM | Approx. 6 Mg | 6000000 |  | Settling chemical (PAC), increase RAS, Lower aeration, and shut off mixers. | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Dry | 2023-05-23 | 00:15 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event |  | Laboratory Data | Approx. 11MGD | Flow meter data | Yes | Housatonic River | 2023-05-23 | 03:00 PM | 1.83 MG | 1830000 |  | Adjust equipment | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 07:15 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | The plant had over 2 inches of rain in a day. Flows exceeded our design flow early on and continue t | UV alarm on SCADA | Undetermined. Still losing solids. It is unclear if the UV dosage reading is accurate at this time. | SCADA flow trend | Yes | Housatonic River | 2023-03-15 | 10:00 AM | Undetermined | 9000000 |  | Rain abated | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Dry | 2023-03-05 | 09:00 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | UV bank overheated and caused the whole system to fail temporarily. | Dosage loss alarm | 297,240 | SCADA flow trend | Yes | Housatonic River | 2023-03-05 | 09:45 PM | 297,240 | 297240 |  | Electrician reset the system. Bank that overheated was taken out of service. | Stratford | 105 Beacon Point Rd, Stratford, CT
STRATFORD | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-26 | 01:15 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Flows for the day averaged over 18 MGD. The plant design flow is 11.5 MGD. | UV alarm for low dosage | Approx. 9 mgals. UV was below minimum required dosage. Some solids loss as well. Final Effluent conc | Flow readings | Yes | Housatonic River | 2023-01-26 | 01:00 PM | 9 mgals | 9000000 |  | Adjusted gates to secondarys as well as flow rates. Added polyaluminum chloride to assist with settl | Stratford | 105 Beacon Point Rd, Stratford, CT
[17 empty] | TOTAL VOLUME | 26127240

## SUFFIELD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SUFFIELD | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-12-11 | 06:15 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | WPCA Operators | 86,000 gallons per hour | Effluent flow meter | Yes | Connecticut River | 2023-12-11 | 07:45 PM | 129,000 gallons | 129000 |  | Rain slowed down | Suffield | 844 East Street S, Suffield, CT
SUFFIELD | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-09-29 | 01:15 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | By an operator at the plant | 166,000 per hour | Flowmeter | Yes | Connecticut River | 2023-09-30 | 02:00 AM | 2,158,000 | 2158000 |  | Flows to the plant subsided | Suffield | 844 East Street S, Suffield, CT
[17 empty] | TOTAL VOLUME | 2287000

## THOMASTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
THOMASTON WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-04-27 | 09:00 AM | Treatment Plant | Sludge Spill | Other | Driver overfilled sludge tanker | sludge came out of tank | 50 gallons | pump rate | Yes | naugatuck river | 2023-04-27 | 09:30 AM | 50-100 Gallons | 75 |  | Truck and parking lot were washed with clean water back to a drain that goes to headworks. Due to th | Thomaston | 200 Old Waterbury Rd, Thomaston, CT
[17 empty] | TOTAL VOLUME | 75

## TORRINGTON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 11:45 AM' | Manhole | Raw Sewage | Excessive Flows - Storm Event | act of god. extreme rain event | routine high water inspections | unknown |  | Yes | naugatuck river | 2023-12-18 | 06:00 PM |  | 3000 |  |  | Torrington | 396 Park Ave, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 09:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Due to heavy rain and polymer pump failure | SCADA alarm | 1.68mgd | 14,000gpm x 120 min | Yes | Naugatuck River | 2023-12-18 | 11:00 AM |  | 1680000 |  |  | Harwinton | 252 Bogue Rd, Harwinton, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 11:45 AM' | Manhole | Raw Sewage | Excessive Flows - Storm Event | act of god. Extreme rain event | routine high water event inspections | unknown |  | No | naugatuck | 2023-12-18 | 06:00 PM |  | 3000 |  |  | Torrington | 107 Scoville St, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:15 PM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event |  | Staff on duty | 21.5 MGD | the current plant rate | Yes | Naugatuck River | 2023-09-30 | 04:00 AM |  | 21500000 |  |  | Harwinton | 252 Bogue Rd, Harwinton, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | rainfall in excess of 4 inches caused sewer main to become surcharged | noticed by collections foreman | 20 GAL / HR | visual estimation | Yes | naugatuck river | 2023-09-30 | 04:00 AM | 260 gallons | 260 |  | rain stopped and flows came down | Torrington | 101 Palmer Bridge St, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | We have <4.5 inches of rainfall since midnight on top of 5.28 inches of rainfall last weekend. | Staff discovered it | ongoing. | unknown | Yes | Naugatuck River | 2023-09-30 | 04:00 AM | 1350 gallons | 1350 |  | rain stopped and flows receded | Torrington | 396 Park Ave, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-09-29 | 03:30 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | One Pump is broken, and one is on order.the high rate flows due to excessive rainfall that we curren | SCADA | unknown 50 gallons per hour | visual estimation | Yes | west branch lead mine brook | 2023-09-30 | 04:00 AM | 625 gallons | 625 |  | rain stopped and flows went down | Torrington | 1096 New Harwinton Rd, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2023-05-15 | 01:15 PM | Pump Station | Raw Sewage | Electrical Equipment Failure | Alarm Communication Failure | WRRF staff checking pumpstations | 500 gallons | Visual estimate | No |  | 2023-05-15 | 03:00 PM | 500 gallons | 500 |  | Our maintenance mechanics replaced the high float and moved the power supply for the comms to anothe | Torrington | 460 Evergreen Rd, Torrington, CT
[17 empty] | TOTAL VOLUME | 23188735
Private Property Bypass - not counted in totals
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2023-02-09 | 00:00 AM | Lateral - Private | Raw Sewage | Unknown | sewer main is not obstructed. must be some sort of blockage in the owners lateral. This SSO was caus | notified by the public that there was sewage on the sidewalk at 53 center st | unknown |  | No |  | 2023-02-13 | 05:00 PM | unknown |  |  | management company had a plumber clear the blockage. The cause of this was not from by a main line b | Torrington | 53 Center St, Torrington, CT

## TRUMBULL
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TRUMBULL | Closed | Sewage Bypass | Dry | 2023-10-10 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Resident called in | under 100 gal estimated trickling out of ground | Best Guess | No |  | 2023-10-10 | 06:30:00 PM | 3,000 gal | 3000 | Visually estimated | Switch over to 10" line at station | Trumbull | 6466 Main St, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2023-09-19 | 08:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Resident saw minor amount of water coming from ground | under 100 Gal | Best guess | No |  | 09/19/2023 | 10:00:00 AM | under 100 Gal | 80 |  | Have switched over to 8 inch line to bypass 10 inch line | Trumbull | 6466 Main St, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2023-07-15 | 09:30 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | on 7-15 -2023 Burns Construction excavated down to the location of the force main no sewage was obse | Notified by Mission pump station monitoring as a high level sump | 5 gpm | observation | Yes | Large inland wetland area leading to Roosevelt Forest | 2023-07-15 | 07:00 PM | 2850 gal | 2850 |  | While no flow from FM was observed in the four test pit locations and no surface flow of sewage see | Trumbull | 135 Merritt Blvd, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2023-07-11 | 08:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Air pocket in force main developed a 3/16 hole in the top of the pipe | The town employee noticed water in the area of our force main | 50 gallons | observation | No |  | 2023-07-11 | 09:30 AM | 50 gallons | 50 |  | Flow was diverted to a secondary force main while the primary main was repaired. Repair couplings | Trumbull | 6466 Main St, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2023-06-24 | 06:45 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Kovacs Construction is responsible for station under construction on by pass with electric Pump and | Kovacs construction has a high wet well alarm that goes out via cell was notified at 6:45pm event en | 2500 gal | best guess due to time frame | Yes | Pequannock river | 2023-06-24 | 07:15 PM | 2500 Gal | 2500 |  | diesel pump was turn onelectric control box Replaced | Trumbull | 2595 Reservoir Ave, Trumbull, CT
[17 empty] | TOTAL VOLUME | 8480

## VERNON
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
VERNON WPCF | Closed | Sewage Bypass | Dry | 2023-04-25 | 10:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Police report by citzen of sewage smell on street | < 50 gallons | by operator at time of cleanup | No |  | 2023-04-25 | 11:30 PM | <50 gallons | 50 |  | Flushed line | Vernon | 14 Grove St, Vernon, CT
VERNON WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-20 | 00:45 AM | Treatment Plant | Raw Sewage | Electrical Equipment Failure | Lightning strike knocked out two legs of utility power. Emergency generator started but failed to tr | Security guard called to notify no power at plant. | 55,500 gallons | Flow rate at time of power outage from intermediate flow meter times minutes overflow occurred. | Yes | Hockanum River | 2023-01-20 | 01:00 AM | 55,500 gallons | 55500 |  | Breakers were manually closed to restore power. Will meet with construction contractor in morning to | Vernon | 100 Windsorville Rd, Vernon, CT
[17 empty] | TOTAL VOLUME | 55550

## WALLINGFORD
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WALLINGFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 09:00 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Wallingford, CT received approximately 3 inches of rain, one week after receiving over 5 inches of r | Crew were dispatched to check on this pump station as it is a known problem area. Upon arrival, th | 900 gallons. Approximately 5 gpm for 180 minutes. | Visual estimate of approximately 5 gallons per minute for 180 minutes = 900 gallons total. | No |  | 2023-12-18 | 12:00 PM | 900 gallons | 900 |  | Vacuum trucks were dispatched to maintain the wet well level and prevent further sewage from overflo | Wallingford | 1030 New Rock Hill Rd, Wallingford, CT
WALLINGFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 10:00 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event |  | The Rotating Biological contactor tanks were found to be overflowing and could not handle a peak flow | 50 gallons per minute | Visual estimate of flow | No |  | 2023-12-18 | 12:15 PM | Approximately 6,000 gallons | 6000 |  | We placed all 6 Secondary clarifiers into service to allow for more tank volume. | Wallingford | 155 John St, Wallingford, CT
WALLINGFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-11 | 05:00 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | Wallingford, CT received 5 inches of rain within a 10-12 hour time frame. 1030 New Rock Hill Road p | High Level Alarm | Approximately 720 gallons | Using best judgement of flow rate around 3 gallons per minute for about 240 minutes. | No |  | 2023-12-11 | 09:00 AM | 720 gallons | 720 |  | Crew was dispatched with vacuum trucks to suck Manhole and Wetwell down to keep up with rain event a | Wallingford | 1030 New Rock Hill Rd, Wallingford, CT
[17 empty] | TOTAL VOLUME | 7620

## WATERBURY
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WATERBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-28 | 11:30 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Excessive rain caused one of the final clarifiers to lose solids. | Operator performing settling test. | Unknown | Unknown | Yes | Naugatuck River | 2023-12-29 | 11:30 AM | Unknown | 10000 |  | Process control around the plant and abnormal high flows decreased. | Waterbury | 210 Municipal Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-12-31 | 10:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | A large rock and wipes were found to be the main issue through CCTV camera work. | The street Dept. contacted WPCF | 2,500 gallons | Visual | No | Hopeville pond brook | 2023-12-31 | 11:00 AM | 4800 gallons | 4800 |  | Jetter truck was dispatched to clear the blockage | Waterbury | 57 Jersey St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 10:45 AM | Treatment Plant | Raw Sewage | Excessive Flows - Storm Event | Abnormal high flows | Operator opened the south junction chamber gate | Unknown | Unknown | Yes | Naugatuck River | 2023-12-18 | 03:15 PM | Unknown | 100000 |  | Gate was closed once flows decreased to less than 84 MG. | Waterbury | 210 Municipal Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-12-18 | 09:30 AM | Pump Station | Raw Sewage | Excessive Flows - Storm Event | excessive flow due to heavy rain event | Collection team visited station due to high level float alarm on SCADA system | 50 GPM | SSO . Manhole estimating overflow rate. | Yes | Welton Brook | 2023-12-18 | 10:30AM | 3,000 gallons | 3000 |  | We maintained until the pumps were able to return to normal . | Waterbury | 60 Terrell Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-11-21 | 11:45 AM' | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Rags and grease found as the cause | Field tech while performing maintenance to the City lines. | 20 gallons | Visual | No |  | 2023-11-21 | 12:15 PM | Final quantity 20 gallons | 20 |  | Blockage was cleared using a jetter truck. Lime was applied to the affected area. | Waterbury | 57 Jersey St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-09-22 | 10:00 AM | Lateral - Private | Raw Sewage | Unknown | a cross connection was discovered during storm line repairs. | When performing storm line and catch basin repairs at the parking lot of Bunker Hill School, a cross | 1,660 gallons per day | 3 month water usage bill, divided by 90 days, times 5 days | Yes | Naugatuck River | 2023-09-26 | 01:30 PM | 8,300 gallons | 8300 |  | The sewer line was connected, and the storm line was capped and plugged. | Waterbury | 170 Bunker Hill Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-09-07 | 12:30 PM | Manhole | Raw Sewage | Other | Collapsed manhole. Trumpet Brook bank caved in and knocked down manhole cone and top. | Resident called collections operator. | 50 GPM | SSO Spill Calculation chart | Yes | Trumpet Brook | 2023-09-07 | 04:30 PM | 12,000 | 12000 |  | By-pass was rerouted, manhole was cleaned out and jetted. Flow was restored. | Waterbury | 611 Bunker Hill Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-04-22 | 02:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Private Curb box. Cause of blockage unknown | Voice mail to WPCF | 200 gallons | Visual by field tech | Yes | Naugatuck river | 2023-04-23 | 11:30 AM | 275 gallons | 275 |  | Landlord hired a contractor to clear the blockage and clean the area with 10% bleach and water. | Waterbury | 553 S Main St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-01-05 | 02:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | CCTV work shows roots as the cause of the blockage in the city line | Q-Alert system put in by homeowner. | 20-30 gallons | Visual by Jacobs field tech | No | N/A | 2023-01-05 | 02:00 PM | 30 gallons | 30 |  | City line was jetted and root cut to remove blockage | Waterbury | 82 Worcester Ave, Waterbury, CT
[17 empty] | TOTAL VOLUME | 138425
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY"S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-03-10 | 08:15 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown blockage in private lateral | Qalert system | 20-30 gallons | visual | No |  | 2023-03-12 | 03:00 PM | DPH estimated 50 gallons. | 50 |  | DPH reports the landlord cleared the blockage and sanitized the area with 10% bleach. | Waterbury | 73 Tudor St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-02-15 | 10:45 AM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | Broken pipe in the private lateral. | Qalert from a passer by | 20-30 gallons | visual | No | N/A | 2023-03-22 | 03:00 PM | DPH reports a final quantity of 150 gallons | 150 |  | A private contractor was hired to dig and repair the broken private lateral. | Waterbury | 27 Oak St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Other | 2023-01-25 | 03:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Blockage in a private curb box | Qalert system | 20-30 gallons | Visual | No |  | 2023-01-26 | 03:00 PM | DPH reports 25 gallons. | 25 |  | DPH Reports the landlord cleared the blockage and cleaned the area with 10% bleach | Waterbury | 65 Rose St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-12-25 | 03:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Private Curb box discharging on to the street | Call from Waterbury Police Dept | 20-30 gallons | Visual | Yes | Naugatuck River | 2023-12-26 | 11:00 AM | DPH reports 75 gallons as the final quantity | 75 |  | DPH reported that the sewage backup was abated and the affected area was clean and sanitized with 10 | Waterbury | 218 Lounsbury St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-12-22 | 10:00 AM | Lateral - Private | Raw Sewage | Other | Blockage in private curb box | Qalert system | 10-20 gallons | visual | No | n/a | 2023-12-24 | 11:00 AM | DPH reports 25 gallons | 25 |  | the sewage backup was abated and the affected area was clean and sanitized with 10% bleach. | Waterbury | 140 Hillside Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-12-04 | 12:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Blockage in the private lateral | DPH notified WPCF | 10-20 gallons | visual | No | N/A | 2023-12-05 | 12:00 PM | DPH estimated 25 gallons. | 25 |  | they got a company out to the property to abate the sewage backup on 12/05/2023 . The sewage backup | Waterbury | 129 Warner St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-12-04 | 03:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Blockage in a private later | Qalert system | 30-40 gallons | Visual | Yes | Naugatuck river | 2023-12-05 | 12:15 PM | DPH reports 50 gallons as the final quantity | 50 |  | The sewage backup was abated and the affected area was clean and sanitized with 10% bleach. | Waterbury | 218 Lounsbury St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-11-29 | 02:45 PM | Lateral - Private | Raw Sewage | Other | Blockage in the private lateral | Qalert system | 20-30 gallons | Visual by field tech | Yes | Mad river | 2023-12-04 | 03:00 PM | DPH reports 75 gallons | 75 |  | DPH reports the sewage backup was abated and the affected area was clean and sanitized with 10% blea | Waterbury | 123 Washington St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-11-21 | 02:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Qalert sewer complaint | 30-40 gallons | Visual | No | n/a | 2023-11-22 | 12:00 PM | DPH reports 50 gallons as the final quantity | 50 |  | DPH reported that • On 11/22/2023, the re-inspection was conducted and the sewage backup was abated | Waterbury | 124 Plaza Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-11-15 | 06:30 AM | Lateral - Private | Raw Sewage | Sewage Line Broken by Contractor or other utility | Private Sewer lateral was broken by a Utility contractor. | Neighbor put in a Qalert | 20-30 gallons | Visual | No | N/A | 2023-12-05 | 12:15 PM | DPH reports 150 gallons | 150 |  | • On 12/5/2023, the re-inspection was conducted and the sewage backup was abated and the affected ar | Waterbury | 50 Hewlett St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-11-06 | 09:00 AM | Lateral - Private | Raw Sewage | Unknown | Unknown at this time | Resident called customer service and a Qalert was received by the collections team. | 30-40 gallons | Visual | No |  | 2023-11-07 | 03:00 PM | DPH estimated 75 gallons. | 75 |  | DPH reports the re-inspection was conducted and the sewage backup was abated and the affected area w | Waterbury | 10-12 Pearl St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-10-30 | 02:00 PM | Lateral - Private | Raw Sewage | Unknown | Unknown at this time | Neighbor called WPCF to complain | 20-30 gallons | Visual | No |  | 2023-10-31 | 09:30 AM | DPH reports 75 gallons for the final quantity | 75 |  | • The inspector got in touch with the landlord and the blockage was cleared. The affected area was c | Waterbury | 68 Randolph Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-10-26 | 08:30 AM | Lateral - Private | Raw Sewage | Other | Blockage in Curb box | Qalert system | 20-40 gallons | visual | No |  | 2023-10-28 | 11:30 AM | DPH estimated the quantity to be 50 gallons | 50 |  | • The inspector got in touch with the landlord and the blockage was cleared. The affected area was | Waterbury | 745 Baldwin St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-10-11 | 12:15 PM | Lateral - Private | Raw Sewage | Unknown | Unknown at this time | Qalert system | 10-20 gallons | visual | No |  | 2023-10-31 | 11:30 AM | DPH reports 100 gallons for final quantity | 100 |  | The re-inspection was conducted and sewer line was repaired and the affected area was clean and sani | Waterbury | 23 Walnut Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-09-28 | 10:30AM | Lateral - Private | Raw Sewage | Unknown | Blockage | Qalert system complaint | 10-30 gallons | Visual | No |  | 2023-10-04 | 05:30 PM | DPH reports final quantity to be 25 gallons | 25 |  | DPH reports The sewage outbreak was abated and the affected area was clean and sanitized with 10% bl | Waterbury | 33 Merrill St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-09-05 | 03:30 PM | Lateral - Private | Raw Sewage | Unknown | unknown at this time | Qalert system | 30-40 gallons | visual | No |  | 2023-09-08 | 03:30 PM | DPH estimates 50 gallons | 50 |  | The landlord hired a contractor to clear the blockage and clean the affected area with 10% bleach an | Waterbury | 36 Hawkins St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-09-01 | 09:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | This is a private lateral. Blockage is unknown. | DPH received a call from a passer by. | 20-30 gallons | Visual | No |  | 2023-09-05 | 05:15 AM | DPH determined final quantity to be 50 gallons. | 50 |  | • The inspector got in touch with the landlord, Notice of Violation was issued because the inspector | Waterbury | 31 Eastwood Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-08-02 | 04:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown at this time. | Qalert system | 5 to 10 Gallons. Ground wet but very little discharge | visual | No |  | 2023-08-04 | 03:30 PM | DPH reports the final quantity to be 10 gallons | 10 |  | The landlord hired a contractor to clear the blockage and clean the affected area with water and 10% | Waterbury | 84 Crown St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-07-17 | 12:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Not known at this time. | Qalert system | 20-30 gallons | Visual | No | N/A | 2023-07-18 | 03:30 PM | DPH estimates the final quantity to be 20 gallons | 20 |  | The landlord hired a contractor to clear the blockage, clean and sanitize the area with 10% bleach. | Waterbury | 23 Bergin Cir, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-06-12 | 09:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown at this time | Qalert system | 20-40 gallons | Visual by field tech. | Yes | Naagatuck river via catch basin | 2023-06-14 | 02:30 PM | DPH estimates final quantity to be 50 gallons | 50 |  | The landlord had the blockage cleared and cleaned the affected area cleaned with 10% bleach and wate | Waterbury | 162 Madison St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-06-07 | 01:15 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Not known at this time | Qalert system | 30-40 gallons | Visual | No |  | 2023-06-27 | 11:30 AM | DPH reports 100 gallons | 100 |  | The DPH inspector got in touch with the landlord and the blockage was cleared on 6/27/2023. The affe | Waterbury | 385 Sylvan Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-06-05 | 03:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Blockage in a private curb box | Qalert system | 15-30 gallons | Visual by field crew | No |  | 2023-06-07 | 09:30 AM | DPH estimated 25 gallons as the final quantity. | 25 |  | Landlord cleared the blockage and had the affected area cleaned with 10 percent and water | Waterbury | 47 Wyman St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-06-05 | 09:30 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Blockage unknown. This is a private lateral. | Field crew noticed when passing by | 30-50 gallons | Visual by field crew | Yes | Naugatuck river | 2023-06-06 | 11:30 AM | DPH reports final quantity to be 25 gallons | 25 |  | The landlord had the blockage cleared and cleaned the affected area with 10% bleach and water | Waterbury | 915 S Main St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-05-31 | 11:45 AM' | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Blockage in a private curb box. | Qalert system | 10-20 gallons | Visual by field tech | No |  | 2023-06-02 | 09:30 AM | DHH reports final quantity to be 100 gallons | 100 |  | landlord had blockage cleared and cleaned affected area with 10% bleach and water. | Waterbury | 7 Rye St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-05-31 | 10:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Private curb box blockage | Qalert system | 10-20 gallons | Visual by Field tech | No |  | 2023-06-02 | 10:30AM | DPH reports 50 gallons | 50 |  | Landlord had the blockage removed and cleaned the affected area with 10% bleach and water | Waterbury | 27 Seminole Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-05-10 | 11:45 AM' | Lateral - Private | Raw Sewage | Unknown | Private lateral blockage or broken lateral pipe | Qalert complaint | 20-40 gallons | visual | No |  | 2023-05-18 | 02:30 PM | DPH reports the final quantity to be 50 gallons | 50 |  | incident was referred to DPH. American Rooter said the private lateral was broken by EverSource and | Waterbury | 184 Meriden Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-04-03 | 02:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Private Sewer Lateral curb box | sewer complaint from Abram - resident | Estimated 20-40 gallons | Visual | No |  | 2023-04-10 | 06:30 PM | DPH reports 50 gallons | 50 |  | the landlord Hired a contractor to clear the blockage. The affected area was clean and sanitized wit | Waterbury | 25 Laurel St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2023-03-29 | 01:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags |  | Qalert system | 20-30 gallons | visual | No | Did not reach a waterbody | 2023-03-31 | 10:30AM | DPH reports 50 gallons | 50 |  | Homeowner hired a contractor to clear the blockage and clean the affected area with 10% bleach and w | Waterbury | 85 Lounsbury Ave, Waterbury, CT

## WEST HAVEN
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WEST HAVEN | Closed | Sewage Bypass | Dry | 2023-06-23 | 10:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease |  | Called In to wpc. By resident | 20 gallons | Visual inspection | No | Possible cove river. | 2023-06-23 | 12:15 PM | 50 to 75 gallons | 60 |  | Brought in city's jet truck and cleared blockage got no response frome property management from both | West Haven | 4 Treat St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2023-11-26 | 10:30AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  |  |  |  | No |  | 2023-11-26 | 11:15 AM | 100 gallons | 100 |  | jetted like removed blockage | West Haven | 129 Beatrice Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2023-07-03 | 01:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Other |  | Homeowner phoned the WPCA. | 100 | Visually | No |  | 2023-07-03 | 02:15 PM | 100 Gallons | 100 |  | Used Vacall truck to free occluded line. | West Haven | 17 High Meadow Ln, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 09:15 PM | Manhole | Raw Sewage | Mechanical Equipment Failure |  | Visually | 100 gallons | Visually | No |  | 2023-03-14 | 09:30 PM | 100 Gallons | 100 |  | Pumps from Cove River PS and bypass pumps shut off. | West Haven | 47 Chestnut St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 05:30 PM | Manhole | Raw Sewage | Mechanical Equipment Failure |  | Visually | 300 Gallons | Visually | No |  | 2023-03-14 | 05:45 PM | 300 Gallons | 300 |  | Pumps at Cove River Pump Station and silent pumps shut off. | West Haven | 104 Chestnut St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2023-03-14 | 03:15 PM | Manhole | Raw Sewage | Mechanical Equipment Failure |  | Visually | 300 gallons | Visually | No |  | 2023-03-14 | 03:30 PM | 300 Gallons | 300 |  | Pumps at Cove River Pump Station and silent pumps on Chestnut St. turned off. | West Haven | 104 Chestnut St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 03:15 PM | Manhole | Raw Sewage | Mechanical Equipment Failure |  | Visually. | 300 gallons | Visually | No |  | 2023-03-14 | 03:45 PM | 300 gallons | 300 |  | Reattached pipe to pump. | West Haven | 104 Chestnut St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-10 | 01:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | excessive flows from storm event/ mechanical failure at pumping station | homeowner visual/ wpc employee visual | 10k gallons to 20k gallons | visual inspection | Yes | cove river | 2023-12-11 | 05:00 PM | 10k to 20k gallons | 15000 |  | storm event subsided and station regain control of flow | West Haven | 427 Painter Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2023-11-22 | 05:00 AM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | Cove River station malfunction due to storm event. | Visually | 10,000 gallons | Visually | Yes | Cove River | 2023-11-22 | 03:00 PM | 10,000 gallons | 10000 |  | Station de-ragged allowing pumps to catch up. | West Haven | 443 Painter Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 10:15 PM | Pump Station | Raw Sewage | Excessive Flows - Storm Event |  | Visually | 540,000 | Visually | Yes | Cove River | 2023-03-16 | 10:00 AM | 540,000 Gallons | 540000 |  | After storm surcharge, control of PS was regained. | West Haven | 360 Kelsey Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2023-03-14 | 10:15 PM | Manhole | Raw Sewage | Other | Pumps were shut off at Cove River to alleviate a previous bypass. | Phone call from resident. | 300-500 Gallons | Visually | Yes | Cove River | 2023-03-14 | 10:30 PM | 500 Gallons | 500 |  | Cove River Pump Station was bypassed. | West Haven | 427 Painter Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-10 | 01:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | ecessive flows from storm | visual inspection | 10k to 20k | visual inspection | Yes | long island sound | 2023-12-11 | 04:30 PM | 10k to 20k gallons | 15000 |  | storm event ended and station regained control of flows | West Haven | 745 Ocean Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2023-01-19 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | homeowner called in bypass | 200 gallons | visual inspection | Yes | long island sound | 2023-01-19 | 10:45 AM | 200 gallons | 200 |  | mechanical issues at pump station.which blocked inlet with grease and rags | West Haven | 1 Templeton St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2023-12-15 | 07:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Other | Broken Plant water line | Water running down parking lot | Approx. 2000 gallons | Visual Estimate | Yes | New Haven Harbor | 2023-12-15 | 08:00 AM | Approx. 2000 gallons | 2000 |  | Closed plant water supply line. | West Haven | 2 Beach St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-17 | 09:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | excessive flows from storm / mechanical failure at pump station | visual inspection | 10k gallons | visual inspection | Yes | old field creek | 2023-12-18 | 07:45 PM | 10k gallons | 10000 |  | storm event ended and station regained control of flows | West Haven | 98 Blohm St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 2-3" per hour | 2023-12-10 | 03:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | storm even heavy rain excessive flows into pump station could not handle flow | visual inspection | 10k to 20k gallons | visual inspection | Yes | old field creek | 2023-12-11 | 05:30 PM | 10k to 20k gallons | 15000 |  | station regained control of flow when storm event ended | West Haven | 96 Blohm St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2023-03-15 | 10:00 AM | Manhole | Raw Sewage | Mechanical Equipment Failure | Bar screen and vfd issues | Call in from resident | 500 to1000 | Visual | Yes | Old field creek | 2023-03-15 | 10:45 AM | 500 to 1000 | 750 |  | Cleared bar screens pumps in hand | West Haven | 165 Blohm St, West Haven, CT
[17 empty] | TOTAL VOLUME | 609710

## WESTPORT
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WESTPORT | Closed | Sewage Bypass | Dry | 2023-11-13 | 00:00 AM | Sewer Main | Raw Sewage | Other | Truck Driver Hit lever before the hose was attached. | police called | 20-50 gallons | estimated | No |  | 2023-11-13 | 03:30 PM | 20-50 gallons | 35 |  | Wash Down The Parking lot. | Westport | 1460 Post Rd E, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2023-11-13 | 11:45 AM' | Manhole | Raw Sewage | Other | Relining a Force main , and 1 truck could not keep up. | Resident called. | 100-200 gallons | estimated | No |  | 2023-11-13 | 12:30 PM | 100-200 gallons | 150 |  | Got additional Trucks. | Westport | 402 Greens Farms Rd, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2023-10-17 | 03:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | while working on Force main | 2000 | estimated | Yes | Stoney Brook | 2023-10-17 | 06:00 PM | 2000 | 2000 |  | Clamp | Westport | 240 Riverside Ave, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2023-09-15 | 04:30 AM | Pump Station | Raw Sewage | Electrical Equipment Failure |  | plumber called the emergency phone | 500 | estimated | Yes | saugatuck river | 2023-09-15 | 06:00 PM | 500 | 500 |  | turned the pumps on ,transfer switch got stuck. | Westport | 605 Riverside Ave, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2023-08-21 | 06:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Broken Sewer Main pipe. | Police Called. | 0-500 Gallons | Estimated | No |  | 2023-08-21 | 04:30 PM | 200 | 200 |  | Repaired Pipe With a Clamp. | Westport | 1680 Post Rd E, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2023-08-21 | 06:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Police called it in. | 0-500 | estimated | No |  | 2023-08-21 | 04:30 PM | 200 | 200 |  | Repaired pipe With a Clamp. | Westport | 1690 Post Rd E, Westport, CT
WESTPORT | Closed | Sewage Bypass | Dry | 2023-05-22 | 02:30 PM | Lateral - Public | Raw Sewage | Sewage Line Blockage - Other | Blockage in gravity line | resident complaint | 0-500 gals | estimated | No |  | 2023-05-22 | 05:45 PM | 500 | 500 |  | Jetted Clogged Line | Westport | 7 Lamplight Ln, Westport, CT
[17 empty] | TOTAL VOLUME | 3585